## SP-C30(수동)
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-C30-PFC-1WS-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 25 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 16 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 1.0 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | METARIALS
17 | FEED NUMBER |  |  | SINGLE |  |  |  | HEAD |  | PP
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | DIAPHRAGM |  | PTFE
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | CHECK BALL |  | CERAMIC
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL GUIDE |  | PP
21 | SUCTION SIZE |  |  | Φ4×Φ6×1m |  |  |  | BALL SEAT |  | FKM
22 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m |  |  |  | JOINT |  | PP
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | O-RING |  | FKM
24 | CONTROLS | [6 empty] | SPRING(VALVE) |  | NONE
25 | TYPE |  |  | MANUAL |  |  |  | HOSE (DIS./SUC.) |  | PE / PVC
26 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | DRIVE (SOLENOID)
27 | ADJUST. RANGE |  |  | 1~100% |  |  |  | POWER CONSUMPTION |  | AVE 15 |  |  | W
28 | [7 empty] | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | [7 empty] | RATED CURRENT |  | 0.4 |  |  | A
30 | WEIGHT |  |  | 2.0 |  |  | kg | INSULATION CLASS |  | F
31 | COLOR | [6 empty] | PROTECTION CLASS |  | IP65
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
34 | SPARE PAERTS | [6 empty] | POWER PLUG |  | NONE
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ACCESSORIES
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
37 | □ | SPRING(VALVE) | [5 empty] | ■ | STRAINER FOOT V/V
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-C30-PFC-1WS-111
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 25 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 16 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 1.0 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | METARIALS
17 | FEED NUMBER |  |  | SINGLE |  |  |  | HEAD |  | PP
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | DIAPHRAGM |  | PTFE
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | CHECK BALL |  | CERAMIC
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL GUIDE |  | PP
21 | SUCTION SIZE |  |  | Φ4×Φ6×1m |  |  |  | BALL SEAT |  | FKM
22 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m |  |  |  | JOINT |  | PP
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | O-RING |  | FKM
24 | CONTROLS | [6 empty] | SPRING(VALVE) |  | NONE
25 | TYPE |  |  | MANUAL |  |  |  | HOSE (DIS./SUC.) |  | PE / PVC
26 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | DRIVE (SOLENOID)
27 | ADJUST. RANGE |  |  | 1~100% |  |  |  | POWER CONSUMPTION |  | AVE 15 |  |  | W
28 | [7 empty] | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | [7 empty] | RATED CURRENT |  | 0.4 |  |  | A
30 | WEIGHT |  |  | 2.1 |  |  | kg | INSULATION CLASS |  | F
31 | COLOR | [6 empty] | PROTECTION CLASS |  | IP65
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
34 | SPARE PAERTS | [6 empty] | POWER PLUG |  | EUROPE 16A 250V
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ACCESSORIES
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
37 | □ | SPRING(VALVE) | [5 empty] | ■ | STRAINER FOOT V/V
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-C30-PFC-1WF-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 25 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 16 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | 16 ±10% |  |  | bar
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 1.0 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | METARIALS
17 | FEED NUMBER |  |  | SINGLE |  |  |  | HEAD |  | PP
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | DIAPHRAGM |  | PTFE
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | CHECK BALL |  | CERAMIC
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL GUIDE |  | PP
21 | SUCTION SIZE |  |  | Φ4×Φ6×1m |  |  |  | BALL SEAT |  | FKM
22 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m |  |  |  | JOINT |  | PP
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | O-RING |  | FKM
24 | CONTROLS | [6 empty] | SPRING(VALVE) |  | NONE
25 | TYPE |  |  | MANUAL |  |  |  | HOSE (DIS./SUC.) |  | PE / PVC
26 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | DRIVE (SOLENOID)
27 | ADJUST. RANGE |  |  | 1~100% |  |  |  | POWER CONSUMPTION |  | AVE 15 |  |  | W
28 | [7 empty] | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | [7 empty] | RATED CURRENT |  | 0.4 |  |  | A
30 | WEIGHT |  |  | 2.0 |  |  | kg | INSULATION CLASS |  | F
31 | COLOR | [6 empty] | PROTECTION CLASS |  | IP65
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
34 | SPARE PAERTS | [6 empty] | POWER PLUG |  | NONE
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ACCESSORIES
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
37 | □ | SPRING(VALVE) | [5 empty] | ■ | STRAINER FOOT V/V
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-C30-PFC-1VS-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 25 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 16 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 300 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 1.0 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | METARIALS
17 | FEED NUMBER |  |  | SINGLE |  |  |  | HEAD |  | PP
18 | VALVE TYPE |  |  | CHECK BALL(SPRING LOADED) |  |  |  | DIAPHRAGM |  | PTFE
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | CHECK BALL |  | CERAMIC
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL GUIDE |  | PP
21 | SUCTION SIZE |  |  | Φ4×Φ6×1m |  |  |  | BALL SEAT |  | FKM
22 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m |  |  |  | JOINT |  | PP
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | O-RING |  | FKM
24 | CONTROLS | [6 empty] | SPRING(VALVE) |  | STS304
25 | TYPE |  |  | MANUAL |  |  |  | HOSE (DIS./SUC.) |  | PE / PVC
26 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | DRIVE (SOLENOID)
27 | ADJUST. RANGE |  |  | 1~100% |  |  |  | POWER CONSUMPTION |  | AVE 15 |  |  | W
28 | [7 empty] | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | [7 empty] | RATED CURRENT |  | 0.4 |  |  | A
30 | WEIGHT |  |  | 2.0 |  |  | kg | INSULATION CLASS |  | F
31 | COLOR | [6 empty] | PROTECTION CLASS |  | IP65
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
34 | SPARE PAERTS | [6 empty] | POWER PLUG |  | NONE
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ACCESSORIES
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
37 | □ | SPRING(VALVE) | [5 empty] | ■ | STRAINER FOOT V/V
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-C30-PFC-2WS-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 25 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 16 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 1.0 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | METARIALS
17 | FEED NUMBER |  |  | SINGLE |  |  |  | HEAD |  | PP
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | DIAPHRAGM |  | PTFE
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | CHECK BALL |  | CERAMIC
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL GUIDE |  | PP
21 | SUCTION SIZE |  |  | Φ4×Φ9×1m |  |  |  | BALL SEAT |  | FKM
22 | DISCHARGE SIZE |  |  | Φ4×Φ9×2m |  |  |  | JOINT |  | PP
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | O-RING |  | FKM
24 | CONTROLS | [6 empty] | SPRING(VALVE) |  | NONE
25 | TYPE |  |  | MANUAL |  |  |  | HOSE (DIS./SUC.) |  | PVC(BRAIDED) / PVC(BRAIDED)
26 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | DRIVE (SOLENOID)
27 | ADJUST. RANGE |  |  | 1~100% |  |  |  | POWER CONSUMPTION |  | AVE 15 |  |  | W
28 | [7 empty] | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | [7 empty] | RATED CURRENT |  | 0.4 |  |  | A
30 | WEIGHT |  |  | 2.0 |  |  | kg | INSULATION CLASS |  | F
31 | COLOR | [6 empty] | PROTECTION CLASS |  | IP65
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
34 | SPARE PAERTS | [6 empty] | POWER PLUG |  | NONE
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ACCESSORIES
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
37 | □ | SPRING(VALVE) | [5 empty] | ■ | STRAINER FOOT V/V
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-C30-PEC-1WS-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 25 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 16 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 1.0 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | METARIALS
17 | FEED NUMBER |  |  | SINGLE |  |  |  | HEAD |  | PP
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | DIAPHRAGM |  | PTFE
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | CHECK BALL |  | CERAMIC
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL GUIDE |  | PP
21 | SUCTION SIZE |  |  | Φ4×Φ6×1m |  |  |  | BALL SEAT |  | EPDM
22 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m |  |  |  | JOINT |  | PP
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | O-RING |  | EPDM
24 | CONTROLS | [6 empty] | SPRING(VALVE) |  | NONE
25 | TYPE |  |  | MANUAL |  |  |  | HOSE (DIS./SUC.) |  | PE / PVC
26 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | DRIVE (SOLENOID)
27 | ADJUST. RANGE |  |  | 1~100% |  |  |  | POWER CONSUMPTION |  | AVE 15 |  |  | W
28 | [7 empty] | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | [7 empty] | RATED CURRENT |  | 0.4 |  |  | A
30 | WEIGHT |  |  | 2.0 |  |  | kg | INSULATION CLASS |  | F
31 | COLOR | [6 empty] | PROTECTION CLASS |  | IP65
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
34 | SPARE PAERTS | [6 empty] | POWER PLUG |  | NONE
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ACCESSORIES
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
37 | □ | SPRING(VALVE) | [5 empty] | ■ | STRAINER FOOT V/V
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-C30-PEC-1WB-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 25 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 16 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 1.0 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | METARIALS
17 | FEED NUMBER |  |  | SINGLE |  |  |  | HEAD |  | PP
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | DIAPHRAGM |  | PTFE
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | CHECK BALL |  | CERAMIC
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL GUIDE |  | PP
21 | SUCTION SIZE |  |  | Φ4×Φ6×1m |  |  |  | BALL SEAT |  | EPDM
22 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m |  |  |  | JOINT |  | PP
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | O-RING |  | EPDM
24 | CONTROLS | [6 empty] | SPRING(VALVE) |  | NONE
25 | TYPE |  |  | MANUAL |  |  |  | HOSE (DIS./SUC.) |  | NYLON / PVC
26 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | DRIVE (SOLENOID)
27 | ADJUST. RANGE |  |  | 1~100% |  |  |  | POWER CONSUMPTION |  | AVE 15 |  |  | W
28 | [7 empty] | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | [7 empty] | RATED CURRENT |  | 0.4 |  |  | A
30 | WEIGHT |  |  | 2.0 |  |  | kg | INSULATION CLASS |  | F
31 | COLOR | [6 empty] | PROTECTION CLASS |  | IP65
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
34 | SPARE PAERTS | [6 empty] | POWER PLUG |  | NONE
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ACCESSORIES
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
37 | □ | SPRING(VALVE) | [5 empty] | ■ | STRAINER FOOT V/V
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-C30-PTC-1WS-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 25 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 16 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 1.0 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | METARIALS
17 | FEED NUMBER |  |  | SINGLE |  |  |  | HEAD |  | PP
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | DIAPHRAGM |  | PTFE
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | CHECK BALL |  | CERAMIC
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL GUIDE |  | PP
21 | SUCTION SIZE |  |  | Φ4×Φ6×1m |  |  |  | BALL SEAT |  | PTFE
22 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m |  |  |  | JOINT |  | PP
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | O-RING |  | FKM
24 | CONTROLS | [6 empty] | SPRING(VALVE) |  | NONE
25 | TYPE |  |  | MANUAL |  |  |  | HOSE (DIS./SUC.) |  | PE / PVC
26 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | DRIVE (SOLENOID)
27 | ADJUST. RANGE |  |  | 1~100% |  |  |  | POWER CONSUMPTION |  | AVE 15 |  |  | W
28 | [7 empty] | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | [7 empty] | RATED CURRENT |  | 0.4 |  |  | A
30 | WEIGHT |  |  | 2.0 |  |  | kg | INSULATION CLASS |  | F
31 | COLOR | [6 empty] | PROTECTION CLASS |  | IP65
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
34 | SPARE PAERTS | [6 empty] | POWER PLUG |  | NONE
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ACCESSORIES
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
37 | □ | SPRING(VALVE) | [5 empty] | ■ | STRAINER FOOT V/V
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-C30-FVC-1WS-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 25 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 16 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 1.0 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | METARIALS
17 | FEED NUMBER |  |  | SINGLE |  |  |  | HEAD |  | PVDF
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | DIAPHRAGM |  | PTFE
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | CHECK BALL |  | CERAMIC
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL GUIDE |  | PVDF
21 | SUCTION SIZE |  |  | Φ4×Φ6×1m |  |  |  | BALL SEAT |  | FKM(ETP)
22 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m |  |  |  | JOINT |  | PVDF
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | O-RING |  | FKM(ETP)
24 | CONTROLS | [6 empty] | SPRING(VALVE) |  | NONE
25 | TYPE |  |  | MANUAL |  |  |  | HOSE (DIS./SUC.) |  | PTFE / PTFE
26 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | DRIVE (SOLENOID)
27 | ADJUST. RANGE |  |  | 1~100% |  |  |  | POWER CONSUMPTION |  | AVE 15 |  |  | W
28 | [7 empty] | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | [7 empty] | RATED CURRENT |  | 0.4 |  |  | A
30 | WEIGHT |  |  | 2.1 |  |  | kg | INSULATION CLASS |  | F
31 | COLOR | [6 empty] | PROTECTION CLASS |  | IP65
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
34 | SPARE PAERTS | [6 empty] | POWER PLUG |  | NONE
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ACCESSORIES
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
37 | □ | SPRING(VALVE) | [5 empty] | ■ | STRAINER FOOT V/V
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-C30-FVC-1WS-111
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 25 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 16 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 1.0 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | METARIALS
17 | FEED NUMBER |  |  | SINGLE |  |  |  | HEAD |  | PVDF
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | DIAPHRAGM |  | PTFE
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | CHECK BALL |  | CERAMIC
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL GUIDE |  | PVDF
21 | SUCTION SIZE |  |  | Φ4×Φ6×1m |  |  |  | BALL SEAT |  | FKM(ETP)
22 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m |  |  |  | JOINT |  | PVDF
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | O-RING |  | FKM(ETP)
24 | CONTROLS | [6 empty] | SPRING(VALVE) |  | NONE
25 | TYPE |  |  | MANUAL |  |  |  | HOSE (DIS./SUC.) |  | PTFE / PTFE
26 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | DRIVE (SOLENOID)
27 | ADJUST. RANGE |  |  | 1~100% |  |  |  | POWER CONSUMPTION |  | AVE 15 |  |  | W
28 | [7 empty] | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | [7 empty] | RATED CURRENT |  | 0.4 |  |  | A
30 | WEIGHT |  |  | 2.1 |  |  | kg | INSULATION CLASS |  | F
31 | COLOR | [6 empty] | PROTECTION CLASS |  | IP65
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
34 | SPARE PAERTS | [6 empty] | POWER PLUG |  | EUROPE 16A 250V
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ACCESSORIES
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
37 | □ | SPRING(VALVE) | [5 empty] | ■ | STRAINER FOOT V/V
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-C30-FTC-1WS-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 25 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 16 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 1.0 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | METARIALS
17 | FEED NUMBER |  |  | SINGLE |  |  |  | HEAD |  | PVDF
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | DIAPHRAGM |  | PTFE
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | CHECK BALL |  | CERAMIC
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL GUIDE |  | PVDF
21 | SUCTION SIZE |  |  | Φ4×Φ6×1m |  |  |  | BALL SEAT |  | PTFE
22 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m |  |  |  | JOINT |  | PVDF
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | O-RING |  | FKM(ETP)
24 | CONTROLS | [6 empty] | SPRING(VALVE) |  | NONE
25 | TYPE |  |  | MANUAL |  |  |  | HOSE (DIS./SUC.) |  | PTFE / PTFE
26 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | DRIVE (SOLENOID)
27 | ADJUST. RANGE |  |  | 1~100% |  |  |  | POWER CONSUMPTION |  | AVE 15 |  |  | W
28 | [7 empty] | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | [7 empty] | RATED CURRENT |  | 0.4 |  |  | A
30 | WEIGHT |  |  | 2.1 |  |  | kg | INSULATION CLASS |  | F
31 | COLOR | [6 empty] | PROTECTION CLASS |  | IP65
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
34 | SPARE PAERTS | [6 empty] | POWER PLUG |  | NONE
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ACCESSORIES
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
37 | □ | SPRING(VALVE) | [5 empty] | ■ | STRAINER FOOT V/V
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.

## SP-C30(자동)
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-C30-PFC-1WS-310
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 25 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 16 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 1.0 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | METARIALS
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | HEAD |  | PP
18 | SUCTION SIZE |  |  | Φ4×Φ6×1m | [6 empty] | DIAPHRAGM |  | PTFE
19 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m | [6 empty] | CHECK BALL |  | CERAMIC
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL GUIDE |  | PP
21 | CONTROLS | [9 empty] | BALL SEAT |  | FKM
22 | TYPE |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | JOINT |  | PP
23 | ADJUST. METHOD |  |  | STROKE SPEED | [6 empty] | O-RING |  | FKM
24 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | SPRING(VALVE) |  | NONE
25 | [10 empty] | HOSE (DIS./SUC.) |  | PE / PVC
26 | SIGNAL | [9 empty] | DRIVE (SOLENOID)
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | POWER CONSUMPTION |  | AVE 15 |  |  | W
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | RATED CURRENT |  | 0.4 |  |  | A
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | INSULATION CLASS |  | F
31 | ■ | LEVEL S/W INPUT |  | □ | REMOTE START/STOP INPUT | [5 empty] | PROTECTION CLASS |  | IP65
32 | □ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | WEIGHT |  |  | 2.1 | [5 empty] | kg | CABLE SIZE |  | 3C×0.75SQ×2m
34 | COLOR | [9 empty] | POWER PLUG |  | NONE
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | SPARE PAERTS
36 | ACCESSORIES | [9 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | CHECK BALL |  | □ | O-RING
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH |  |  |  | □ | SPRING(VALVE)
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-C30-PFC-1WS-410
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 25 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 16 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 1.0 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | METARIALS
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | HEAD |  | PP
18 | SUCTION SIZE |  |  | Φ4×Φ6×1m | [6 empty] | DIAPHRAGM |  | PTFE
19 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m | [6 empty] | CHECK BALL |  | CERAMIC
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL GUIDE |  | PP
21 | CONTROLS | [9 empty] | BALL SEAT |  | FKM
22 | TYPE |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | JOINT |  | PP
23 | ADJUST. METHOD |  |  | STROKE SPEED | [6 empty] | O-RING |  | FKM
24 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | SPRING(VALVE) |  | NONE
25 | [10 empty] | HOSE (DIS./SUC.) |  | PE / PVC
26 | SIGNAL | [9 empty] | DRIVE (SOLENOID)
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | POWER CONSUMPTION |  | AVE 15 |  |  | W
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | RATED CURRENT |  | 0.4 |  |  | A
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | INSULATION CLASS |  | F
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE START/STOP INPUT | [5 empty] | PROTECTION CLASS |  | IP65
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | WEIGHT |  |  | 2.1 | [5 empty] | kg | CABLE SIZE |  | 3C×0.75SQ×2m
34 | COLOR | [9 empty] | POWER PLUG |  | NONE
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | SPARE PAERTS
36 | ACCESSORIES | [9 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | CHECK BALL |  | □ | O-RING
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH |  |  |  | □ | SPRING(VALVE)
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-C30-PFC-1WS-311
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 25 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 16 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 1.0 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | METARIALS
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | HEAD |  | PP
18 | SUCTION SIZE |  |  | Φ4×Φ6×1m | [6 empty] | DIAPHRAGM |  | PTFE
19 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m | [6 empty] | CHECK BALL |  | CERAMIC
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL GUIDE |  | PP
21 | CONTROLS | [9 empty] | BALL SEAT |  | FKM
22 | TYPE |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | JOINT |  | PP
23 | ADJUST. METHOD |  |  | STROKE SPEED | [6 empty] | O-RING |  | FKM
24 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | SPRING(VALVE) |  | NONE
25 | [10 empty] | HOSE (DIS./SUC.) |  | PE / PVC
26 | SIGNAL | [9 empty] | DRIVE (SOLENOID)
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | POWER CONSUMPTION |  | AVE 15 |  |  | W
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | RATED CURRENT |  | 0.4 |  |  | A
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | INSULATION CLASS |  | F
31 | ■ | LEVEL S/W INPUT |  | □ | REMOTE START/STOP INPUT | [5 empty] | PROTECTION CLASS |  | IP65
32 | □ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | WEIGHT |  |  | 2.1 | [5 empty] | kg | CABLE SIZE |  | 3C×0.75SQ×2m
34 | COLOR | [9 empty] | POWER PLUG |  | EUROPE 16A 250V
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | SPARE PAERTS
36 | ACCESSORIES | [9 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | CHECK BALL |  | □ | O-RING
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH |  |  |  | □ | SPRING(VALVE)
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-C30-PFC-1WS-411
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 25 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 16 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 1.0 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | METARIALS
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | HEAD |  | PP
18 | SUCTION SIZE |  |  | Φ4×Φ6×1m | [6 empty] | DIAPHRAGM |  | PTFE
19 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m | [6 empty] | CHECK BALL |  | CERAMIC
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL GUIDE |  | PP
21 | CONTROLS | [9 empty] | BALL SEAT |  | FKM
22 | TYPE |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | JOINT |  | PP
23 | ADJUST. METHOD |  |  | STROKE SPEED | [6 empty] | O-RING |  | FKM
24 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | SPRING(VALVE) |  | NONE
25 | [10 empty] | HOSE (DIS./SUC.) |  | PE / PVC
26 | SIGNAL | [9 empty] | DRIVE (SOLENOID)
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | POWER CONSUMPTION |  | AVE 15 |  |  | W
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | RATED CURRENT |  | 0.4 |  |  | A
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | INSULATION CLASS |  | F
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE START/STOP INPUT | [5 empty] | PROTECTION CLASS |  | IP65
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | WEIGHT |  |  | 2.1 | [5 empty] | kg | CABLE SIZE |  | 3C×0.75SQ×2m
34 | COLOR | [9 empty] | POWER PLUG |  | EUROPE 16A 250V
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | SPARE PAERTS
36 | ACCESSORIES | [9 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | CHECK BALL |  | □ | O-RING
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH |  |  |  | □ | SPRING(VALVE)
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-C30-FVC-1WS-310
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 25 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 16 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 1.0 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | METARIALS
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | HEAD |  | PVDF
18 | SUCTION SIZE |  |  | Φ4×Φ6×1m | [6 empty] | DIAPHRAGM |  | PTFE
19 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m | [6 empty] | CHECK BALL |  | CERAMIC
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL GUIDE |  | PVDF
21 | CONTROLS | [9 empty] | BALL SEAT |  | FKM(ETP)
22 | TYPE |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | JOINT |  | PVDF
23 | ADJUST. METHOD |  |  | STROKE SPEED | [6 empty] | O-RING |  | FKM(ETP)
24 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | SPRING(VALVE) |  | NONE
25 | [10 empty] | HOSE (DIS./SUC.) |  | PTFE / PTFE
26 | SIGNAL | [9 empty] | DRIVE (SOLENOID)
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | POWER CONSUMPTION |  | AVE 15 |  |  | W
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | RATED CURRENT |  | 0.4 |  |  | A
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | INSULATION CLASS |  | F
31 | ■ | LEVEL S/W INPUT |  | □ | REMOTE START/STOP INPUT | [5 empty] | PROTECTION CLASS |  | IP65
32 | □ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | WEIGHT |  |  | 2.2 | [5 empty] | kg | CABLE SIZE |  | 3C×0.75SQ×2m
34 | COLOR | [9 empty] | POWER PLUG |  | NONE
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | SPARE PAERTS
36 | ACCESSORIES | [9 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | CHECK BALL |  | □ | O-RING
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH |  |  |  | □ | SPRING(VALVE)
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-C30-FVC-1WS-410
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 25 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 16 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 1.0 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | METARIALS
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | HEAD |  | PVDF
18 | SUCTION SIZE |  |  | Φ4×Φ6×1m | [6 empty] | DIAPHRAGM |  | PTFE
19 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m | [6 empty] | CHECK BALL |  | CERAMIC
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL GUIDE |  | PVDF
21 | CONTROLS | [9 empty] | BALL SEAT |  | FKM(ETP)
22 | TYPE |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | JOINT |  | PVDF
23 | ADJUST. METHOD |  |  | STROKE SPEED | [6 empty] | O-RING |  | FKM(ETP)
24 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | SPRING(VALVE) |  | NONE
25 | [10 empty] | HOSE (DIS./SUC.) |  | PTFE / PTFE
26 | SIGNAL | [9 empty] | DRIVE (SOLENOID)
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | POWER CONSUMPTION |  | AVE 15 |  |  | W
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | RATED CURRENT |  | 0.4 |  |  | A
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | INSULATION CLASS |  | F
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE START/STOP INPUT | [5 empty] | PROTECTION CLASS |  | IP65
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | WEIGHT |  |  | 2.2 | [5 empty] | kg | CABLE SIZE |  | 3C×0.75SQ×2m
34 | COLOR | [9 empty] | POWER PLUG |  | NONE
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | SPARE PAERTS
36 | ACCESSORIES | [9 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | CHECK BALL |  | □ | O-RING
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH |  |  |  | □ | SPRING(VALVE)
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-C30-FVC-1WS-311
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 25 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 16 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 1.0 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | METARIALS
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | HEAD |  | PVDF
18 | SUCTION SIZE |  |  | Φ4×Φ6×1m | [6 empty] | DIAPHRAGM |  | PTFE
19 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m | [6 empty] | CHECK BALL |  | CERAMIC
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL GUIDE |  | PVDF
21 | CONTROLS | [9 empty] | BALL SEAT |  | FKM(ETP)
22 | TYPE |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | JOINT |  | PVDF
23 | ADJUST. METHOD |  |  | STROKE SPEED | [6 empty] | O-RING |  | FKM(ETP)
24 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | SPRING(VALVE) |  | NONE
25 | [10 empty] | HOSE (DIS./SUC.) |  | PTFE / PTFE
26 | SIGNAL | [9 empty] | DRIVE (SOLENOID)
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | POWER CONSUMPTION |  | AVE 15 |  |  | W
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | RATED CURRENT |  | 0.4 |  |  | A
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | INSULATION CLASS |  | F
31 | ■ | LEVEL S/W INPUT |  | □ | REMOTE START/STOP INPUT | [5 empty] | PROTECTION CLASS |  | IP65
32 | □ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | WEIGHT |  |  | 2.2 | [5 empty] | kg | CABLE SIZE |  | 3C×0.75SQ×2m
34 | COLOR | [9 empty] | POWER PLUG |  | EUROPE 16A 250V
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | SPARE PAERTS
36 | ACCESSORIES | [9 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | CHECK BALL |  | □ | O-RING
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH |  |  |  | □ | SPRING(VALVE)
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-C30-FVC-1WS-411
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 25 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 16 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 1.0 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | METARIALS
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | HEAD |  | PVDF
18 | SUCTION SIZE |  |  | Φ4×Φ6×1m | [6 empty] | DIAPHRAGM |  | PTFE
19 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m | [6 empty] | CHECK BALL |  | CERAMIC
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL GUIDE |  | PVDF
21 | CONTROLS | [9 empty] | BALL SEAT |  | FKM(ETP)
22 | TYPE |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | JOINT |  | PVDF
23 | ADJUST. METHOD |  |  | STROKE SPEED | [6 empty] | O-RING |  | FKM(ETP)
24 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | SPRING(VALVE) |  | NONE
25 | [10 empty] | HOSE (DIS./SUC.) |  | PTFE / PTFE
26 | SIGNAL | [9 empty] | DRIVE (SOLENOID)
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | POWER CONSUMPTION |  | AVE 15 |  |  | W
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | RATED CURRENT |  | 0.4 |  |  | A
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | INSULATION CLASS |  | F
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE START/STOP INPUT | [5 empty] | PROTECTION CLASS |  | IP65
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | WEIGHT |  |  | 2.2 | [5 empty] | kg | CABLE SIZE |  | 3C×0.75SQ×2m
34 | COLOR | [9 empty] | POWER PLUG |  | EUROPE 16A 250V
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | SPARE PAERTS
36 | ACCESSORIES | [9 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | CHECK BALL |  | □ | O-RING
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH |  |  |  | □ | SPRING(VALVE)
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.

## SP-C50(수동)
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-C50-PFC-1WS-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 55 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 12 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | METARIALS
17 | FEED NUMBER |  |  | SINGLE |  |  |  | HEAD |  | PP
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | DIAPHRAGM |  | PTFE
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | CHECK BALL |  | CERAMIC
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL GUIDE |  | PP
21 | SUCTION SIZE |  |  | Φ4×Φ6×1m |  |  |  | BALL SEAT |  | FKM
22 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m |  |  |  | JOINT |  | PP
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | O-RING |  | FKM
24 | CONTROLS | [6 empty] | SPRING(VALVE) |  | NONE
25 | TYPE |  |  | MANUAL |  |  |  | HOSE (DIS./SUC.) |  | PE / PVC
26 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | DRIVE (SOLENOID)
27 | ADJUST. RANGE |  |  | 1~100% |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | [7 empty] | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | [7 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | WEIGHT |  |  | 2.4 |  |  | kg | INSULATION CLASS |  | F
31 | COLOR | [6 empty] | PROTECTION CLASS |  | IP65
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
34 | SPARE PAERTS | [6 empty] | POWER PLUG |  | NONE
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ACCESSORIES
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
37 | □ | SPRING(VALVE) | [5 empty] | ■ | STRAINER FOOT V/V
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-C50-PFC-1WS-111
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 55 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 12 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | METARIALS
17 | FEED NUMBER |  |  | SINGLE |  |  |  | HEAD |  | PP
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | DIAPHRAGM |  | PTFE
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | CHECK BALL |  | CERAMIC
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL GUIDE |  | PP
21 | SUCTION SIZE |  |  | Φ4×Φ6×1m |  |  |  | BALL SEAT |  | FKM
22 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m |  |  |  | JOINT |  | PP
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | O-RING |  | FKM
24 | CONTROLS | [6 empty] | SPRING(VALVE) |  | NONE
25 | TYPE |  |  | MANUAL |  |  |  | HOSE (DIS./SUC.) |  | PE / PVC
26 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | DRIVE (SOLENOID)
27 | ADJUST. RANGE |  |  | 1~100% |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | [7 empty] | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | [7 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | WEIGHT |  |  | 2.4 |  |  | kg | INSULATION CLASS |  | F
31 | COLOR | [6 empty] | PROTECTION CLASS |  | IP65
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
34 | SPARE PAERTS | [6 empty] | POWER PLUG |  | EUROPE 16A 250V
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ACCESSORIES
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
37 | □ | SPRING(VALVE) | [5 empty] | ■ | STRAINER FOOT V/V
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-C50-PFC-1WF-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 55 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 12 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | 12 ±10% |  |  | bar
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | METARIALS
17 | FEED NUMBER |  |  | SINGLE |  |  |  | HEAD |  | PP
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | DIAPHRAGM |  | PTFE
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | CHECK BALL |  | CERAMIC
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL GUIDE |  | PP
21 | SUCTION SIZE |  |  | Φ4×Φ6×1m |  |  |  | BALL SEAT |  | FKM
22 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m |  |  |  | JOINT |  | PP
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | O-RING |  | FKM
24 | CONTROLS | [6 empty] | SPRING(VALVE) |  | NONE
25 | TYPE |  |  | MANUAL |  |  |  | HOSE (DIS./SUC.) |  | PE / PVC
26 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | DRIVE (SOLENOID)
27 | ADJUST. RANGE |  |  | 1~100% |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | [7 empty] | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | [7 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | WEIGHT |  |  | 2.4 |  |  | kg | INSULATION CLASS |  | F
31 | COLOR | [6 empty] | PROTECTION CLASS |  | IP65
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
34 | SPARE PAERTS | [6 empty] | POWER PLUG |  | NONE
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ACCESSORIES
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
37 | □ | SPRING(VALVE) | [5 empty] | ■ | STRAINER FOOT V/V
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-C50-PFC-1VS-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 55 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 12 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 300 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | METARIALS
17 | FEED NUMBER |  |  | SINGLE |  |  |  | HEAD |  | PP
18 | VALVE TYPE |  |  | CHECK BALL(SPRING LOADED) |  |  |  | DIAPHRAGM |  | PTFE
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | CHECK BALL |  | CERAMIC
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL GUIDE |  | PP
21 | SUCTION SIZE |  |  | Φ4×Φ6×1m |  |  |  | BALL SEAT |  | FKM
22 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m |  |  |  | JOINT |  | PP
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | O-RING |  | FKM
24 | CONTROLS | [6 empty] | SPRING(VALVE) |  | STS304
25 | TYPE |  |  | MANUAL |  |  |  | HOSE (DIS./SUC.) |  | PE / PVC
26 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | DRIVE (SOLENOID)
27 | ADJUST. RANGE |  |  | 1~100% |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | [7 empty] | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | [7 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | WEIGHT |  |  | 2.4 |  |  | kg | INSULATION CLASS |  | F
31 | COLOR | [6 empty] | PROTECTION CLASS |  | IP65
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
34 | SPARE PAERTS | [6 empty] | POWER PLUG |  | NONE
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ACCESSORIES
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
37 | □ | SPRING(VALVE) | [5 empty] | ■ | STRAINER FOOT V/V
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-C50-PFC-2WS-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 55 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 12 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | METARIALS
17 | FEED NUMBER |  |  | SINGLE |  |  |  | HEAD |  | PP
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | DIAPHRAGM |  | PTFE
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | CHECK BALL |  | CERAMIC
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL GUIDE |  | PP
21 | SUCTION SIZE |  |  | Φ4×Φ9×1m |  |  |  | BALL SEAT |  | FKM
22 | DISCHARGE SIZE |  |  | Φ4×Φ9×2m |  |  |  | JOINT |  | PP
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | O-RING |  | FKM
24 | CONTROLS | [6 empty] | SPRING(VALVE) |  | NONE
25 | TYPE |  |  | MANUAL |  |  |  | HOSE (DIS./SUC.) |  | PVC(BRAIDED) / PVC(BRAIDED)
26 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | DRIVE (SOLENOID)
27 | ADJUST. RANGE |  |  | 1~100% |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | [7 empty] | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | [7 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | WEIGHT |  |  | 2.4 |  |  | kg | INSULATION CLASS |  | F
31 | COLOR | [6 empty] | PROTECTION CLASS |  | IP65
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
34 | SPARE PAERTS | [6 empty] | POWER PLUG |  | NONE
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ACCESSORIES
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
37 | □ | SPRING(VALVE) | [5 empty] | ■ | STRAINER FOOT V/V
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-C50-PEC-1WS-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 55 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 12 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | METARIALS
17 | FEED NUMBER |  |  | SINGLE |  |  |  | HEAD |  | PP
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | DIAPHRAGM |  | PTFE
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | CHECK BALL |  | CERAMIC
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL GUIDE |  | PP
21 | SUCTION SIZE |  |  | Φ4×Φ6×1m |  |  |  | BALL SEAT |  | EPDM
22 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m |  |  |  | JOINT |  | PP
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | O-RING |  | EPDM
24 | CONTROLS | [6 empty] | SPRING(VALVE) |  | NONE
25 | TYPE |  |  | MANUAL |  |  |  | HOSE (DIS./SUC.) |  | PE / PVC
26 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | DRIVE (SOLENOID)
27 | ADJUST. RANGE |  |  | 1~100% |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | [7 empty] | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | [7 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | WEIGHT |  |  | 2.4 |  |  | kg | INSULATION CLASS |  | F
31 | COLOR | [6 empty] | PROTECTION CLASS |  | IP65
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
34 | SPARE PAERTS | [6 empty] | POWER PLUG |  | NONE
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ACCESSORIES
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
37 | □ | SPRING(VALVE) | [5 empty] | ■ | STRAINER FOOT V/V
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-C50-PEC-1WB-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 55 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 12 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | METARIALS
17 | FEED NUMBER |  |  | SINGLE |  |  |  | HEAD |  | PP
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | DIAPHRAGM |  | PTFE
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | CHECK BALL |  | CERAMIC
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL GUIDE |  | PP
21 | SUCTION SIZE |  |  | Φ4×Φ6×1m |  |  |  | BALL SEAT |  | EPDM
22 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m |  |  |  | JOINT |  | PP
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | O-RING |  | EPDM
24 | CONTROLS | [6 empty] | SPRING(VALVE) |  | NONE
25 | TYPE |  |  | MANUAL |  |  |  | HOSE (DIS./SUC.) |  | NYLON / PVC
26 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | DRIVE (SOLENOID)
27 | ADJUST. RANGE |  |  | 1~100% |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | [7 empty] | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | [7 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | WEIGHT |  |  | 2.4 |  |  | kg | INSULATION CLASS |  | F
31 | COLOR | [6 empty] | PROTECTION CLASS |  | IP65
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
34 | SPARE PAERTS | [6 empty] | POWER PLUG |  | NONE
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ACCESSORIES
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
37 | □ | SPRING(VALVE) | [5 empty] | ■ | STRAINER FOOT V/V
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-C50-FVC-1WS-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 55 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 12 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | METARIALS
17 | FEED NUMBER |  |  | SINGLE |  |  |  | HEAD |  | PVDF
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | DIAPHRAGM |  | PTFE
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | CHECK BALL |  | CERAMIC
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL GUIDE |  | PVDF
21 | SUCTION SIZE |  |  | Φ4×Φ6×1m |  |  |  | BALL SEAT |  | FKM(ETP)
22 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m |  |  |  | JOINT |  | PVDF
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | O-RING |  | FKM(ETP)
24 | CONTROLS | [6 empty] | SPRING(VALVE) |  | NONE
25 | TYPE |  |  | MANUAL |  |  |  | HOSE (DIS./SUC.) |  | PTFE / PTFE
26 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | DRIVE (SOLENOID)
27 | ADJUST. RANGE |  |  | 1~100% |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | [7 empty] | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | [7 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | WEIGHT |  |  | 2.5 |  |  | kg | INSULATION CLASS |  | F
31 | COLOR | [6 empty] | PROTECTION CLASS |  | IP65
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
34 | SPARE PAERTS | [6 empty] | POWER PLUG |  | NONE
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ACCESSORIES
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
37 | □ | SPRING(VALVE) | [5 empty] | ■ | STRAINER FOOT V/V
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-C50-FVC-1WS-111
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 55 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 12 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | METARIALS
17 | FEED NUMBER |  |  | SINGLE |  |  |  | HEAD |  | PVDF
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | DIAPHRAGM |  | PTFE
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | CHECK BALL |  | CERAMIC
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL GUIDE |  | PVDF
21 | SUCTION SIZE |  |  | Φ4×Φ6×1m |  |  |  | BALL SEAT |  | FKM(ETP)
22 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m |  |  |  | JOINT |  | PVDF
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | O-RING |  | FKM(ETP)
24 | CONTROLS | [6 empty] | SPRING(VALVE) |  | NONE
25 | TYPE |  |  | MANUAL |  |  |  | HOSE (DIS./SUC.) |  | PTFE / PTFE
26 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | DRIVE (SOLENOID)
27 | ADJUST. RANGE |  |  | 1~100% |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | [7 empty] | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | [7 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | WEIGHT |  |  | 2.5 |  |  | kg | INSULATION CLASS |  | F
31 | COLOR | [6 empty] | PROTECTION CLASS |  | IP65
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
34 | SPARE PAERTS | [6 empty] | POWER PLUG |  | EUROPE 16A 250V
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ACCESSORIES
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
37 | □ | SPRING(VALVE) | [5 empty] | ■ | STRAINER FOOT V/V
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.

## SP-C50(자동)
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-C50-PFC-1WS-310
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 55 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 12 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | METARIALS
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | HEAD |  | PP
18 | SUCTION SIZE |  |  | Φ4×Φ6×1m | [6 empty] | DIAPHRAGM |  | PTFE
19 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m | [6 empty] | CHECK BALL |  | CERAMIC
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL GUIDE |  | PP
21 | CONTROLS | [9 empty] | BALL SEAT |  | FKM
22 | TYPE |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | JOINT |  | PP
23 | ADJUST. METHOD |  |  | STROKE SPEED | [6 empty] | O-RING |  | FKM
24 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | SPRING(VALVE) |  | NONE
25 | [10 empty] | HOSE (DIS./SUC.) |  | PE / PVC
26 | SIGNAL | [9 empty] | DRIVE (SOLENOID)
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | INSULATION CLASS |  | F
31 | ■ | LEVEL S/W INPUT |  | □ | REMOTE START/STOP INPUT | [5 empty] | PROTECTION CLASS |  | IP65
32 | □ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | WEIGHT |  |  | 2.4 | [5 empty] | kg | CABLE SIZE |  | 3C×0.75SQ×2m
34 | COLOR | [9 empty] | POWER PLUG |  | NONE
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | SPARE PAERTS
36 | ACCESSORIES | [9 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | CHECK BALL |  | □ | O-RING
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH |  |  |  | □ | SPRING(VALVE)
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-C50-PFC-1WS-410
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 55 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 12 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | METARIALS
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | HEAD |  | PP
18 | SUCTION SIZE |  |  | Φ4×Φ6×1m | [6 empty] | DIAPHRAGM |  | PTFE
19 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m | [6 empty] | CHECK BALL |  | CERAMIC
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL GUIDE |  | PP
21 | CONTROLS | [9 empty] | BALL SEAT |  | FKM
22 | TYPE |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | JOINT |  | PP
23 | ADJUST. METHOD |  |  | STROKE SPEED | [6 empty] | O-RING |  | FKM
24 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | SPRING(VALVE) |  | NONE
25 | [10 empty] | HOSE (DIS./SUC.) |  | PE / PVC
26 | SIGNAL | [9 empty] | DRIVE (SOLENOID)
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | INSULATION CLASS |  | F
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE RUN/STOP INPUT | [5 empty] | PROTECTION CLASS |  | IP65
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | WEIGHT |  |  | 2.4 | [5 empty] | kg | CABLE SIZE |  | 3C×0.75SQ×2m
34 | COLOR | [9 empty] | POWER PLUG |  | NONE
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | SPARE PAERTS
36 | ACCESSORIES | [9 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | CHECK BALL |  | □ | O-RING
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH |  |  |  | □ | SPRING(VALVE)
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-C50-PFC-1WS-311
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 55 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 12 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | METARIALS
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | HEAD |  | PP
18 | SUCTION SIZE |  |  | Φ4×Φ6×1m | [6 empty] | DIAPHRAGM |  | PTFE
19 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m | [6 empty] | CHECK BALL |  | CERAMIC
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL GUIDE |  | PP
21 | CONTROLS | [9 empty] | BALL SEAT |  | FKM
22 | TYPE |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | JOINT |  | PP
23 | ADJUST. METHOD |  |  | STROKE SPEED | [6 empty] | O-RING |  | FKM
24 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | SPRING(VALVE) |  | NONE
25 | [10 empty] | HOSE (DIS./SUC.) |  | PE / PVC
26 | SIGNAL | [9 empty] | DRIVE (SOLENOID)
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | INSULATION CLASS |  | F
31 | ■ | LEVEL S/W INPUT |  | □ | REMOTE START/STOP INPUT | [5 empty] | PROTECTION CLASS |  | IP65
32 | □ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | WEIGHT |  |  | 2.4 | [5 empty] | kg | CABLE SIZE |  | 3C×0.75SQ×2m
34 | COLOR | [9 empty] | POWER PLUG |  | EUROPE 16A 250V
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | SPARE PAERTS
36 | ACCESSORIES | [9 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | CHECK BALL |  | □ | O-RING
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH |  |  |  | □ | SPRING(VALVE)
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-C50-PFC-1WS-411
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 55 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 12 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | METARIALS
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | HEAD |  | PP
18 | SUCTION SIZE |  |  | Φ4×Φ6×1m | [6 empty] | DIAPHRAGM |  | PTFE
19 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m | [6 empty] | CHECK BALL |  | CERAMIC
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL GUIDE |  | PP
21 | CONTROLS | [9 empty] | BALL SEAT |  | FKM
22 | TYPE |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | JOINT |  | PP
23 | ADJUST. METHOD |  |  | STROKE SPEED | [6 empty] | O-RING |  | FKM
24 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | SPRING(VALVE) |  | NONE
25 | [10 empty] | HOSE (DIS./SUC.) |  | PE / PVC
26 | SIGNAL | [9 empty] | DRIVE (SOLENOID)
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | INSULATION CLASS |  | F
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE RUN/STOP INPUT | [5 empty] | PROTECTION CLASS |  | IP65
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | WEIGHT |  |  | 2.4 | [5 empty] | kg | CABLE SIZE |  | 3C×0.75SQ×2m
34 | COLOR | [9 empty] | POWER PLUG |  | EUROPE 16A 250V
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | SPARE PAERTS
36 | ACCESSORIES | [9 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | CHECK BALL |  | □ | O-RING
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH |  |  |  | □ | SPRING(VALVE)
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-C50-FVC-1WS-310
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 55 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 12 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | METARIALS
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | HEAD |  | PVDF
18 | SUCTION SIZE |  |  | Φ4×Φ6×1m | [6 empty] | DIAPHRAGM |  | PTFE
19 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m | [6 empty] | CHECK BALL |  | CERAMIC
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL GUIDE |  | PVDF
21 | CONTROLS | [9 empty] | BALL SEAT |  | FKM(ETP)
22 | TYPE |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | JOINT |  | PVDF
23 | ADJUST. METHOD |  |  | STROKE SPEED | [6 empty] | O-RING |  | FKM(ETP)
24 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | SPRING(VALVE) |  | NONE
25 | [10 empty] | HOSE (DIS./SUC.) |  | PTFE / PTFE
26 | SIGNAL | [9 empty] | DRIVE (SOLENOID)
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | INSULATION CLASS |  | F
31 | ■ | LEVEL S/W INPUT |  | □ | REMOTE START/STOP INPUT | [5 empty] | PROTECTION CLASS |  | IP65
32 | □ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | WEIGHT |  |  | 2.4 | [5 empty] | kg | CABLE SIZE |  | 3C×0.75SQ×2m
34 | COLOR | [9 empty] | POWER PLUG |  | NONE
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | SPARE PAERTS
36 | ACCESSORIES | [9 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | CHECK BALL |  | □ | O-RING
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH |  |  |  | □ | SPRING(VALVE)
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-C50-FVC-1WS-410
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 55 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 12 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | METARIALS
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | HEAD |  | PVDF
18 | SUCTION SIZE |  |  | Φ4×Φ6×1m | [6 empty] | DIAPHRAGM |  | PTFE
19 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m | [6 empty] | CHECK BALL |  | CERAMIC
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL GUIDE |  | PVDF
21 | CONTROLS | [9 empty] | BALL SEAT |  | FKM(ETP)
22 | TYPE |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | JOINT |  | PVDF
23 | ADJUST. METHOD |  |  | STROKE SPEED | [6 empty] | O-RING |  | FKM(ETP)
24 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | SPRING(VALVE) |  | NONE
25 | [10 empty] | HOSE (DIS./SUC.) |  | PTFE / PTFE
26 | SIGNAL | [9 empty] | DRIVE (SOLENOID)
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | INSULATION CLASS |  | F
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE RUN/STOP INPUT | [5 empty] | PROTECTION CLASS |  | IP65
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | WEIGHT |  |  | 2.4 | [5 empty] | kg | CABLE SIZE |  | 3C×0.75SQ×2m
34 | COLOR | [9 empty] | POWER PLUG |  | NONE
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | SPARE PAERTS
36 | ACCESSORIES | [9 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | CHECK BALL |  | □ | O-RING
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH |  |  |  | □ | SPRING(VALVE)
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-C50-FVC-1WS-311
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 55 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 12 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | METARIALS
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | HEAD |  | PVDF
18 | SUCTION SIZE |  |  | Φ4×Φ6×1m | [6 empty] | DIAPHRAGM |  | PTFE
19 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m | [6 empty] | CHECK BALL |  | CERAMIC
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL GUIDE |  | PVDF
21 | CONTROLS | [9 empty] | BALL SEAT |  | FKM(ETP)
22 | TYPE |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | JOINT |  | PVDF
23 | ADJUST. METHOD |  |  | STROKE SPEED | [6 empty] | O-RING |  | FKM(ETP)
24 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | SPRING(VALVE) |  | NONE
25 | [10 empty] | HOSE (DIS./SUC.) |  | PTFE / PTFE
26 | SIGNAL | [9 empty] | DRIVE (SOLENOID)
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | INSULATION CLASS |  | F
31 | ■ | LEVEL S/W INPUT |  | □ | REMOTE START/STOP INPUT | [5 empty] | PROTECTION CLASS |  | IP65
32 | □ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | WEIGHT |  |  | 2.5 | [5 empty] | kg | CABLE SIZE |  | 3C×0.75SQ×2m
34 | COLOR | [9 empty] | POWER PLUG |  | EUROPE 16A 250V
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | SPARE PAERTS
36 | ACCESSORIES | [9 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | CHECK BALL |  | □ | O-RING
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH |  |  |  | □ | SPRING(VALVE)
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-C50-FVC-1WS-411
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 55 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 12 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1.0 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 50 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | METARIALS
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | HEAD |  | PVDF
18 | SUCTION SIZE |  |  | Φ4×Φ6×1m | [6 empty] | DIAPHRAGM |  | PTFE
19 | DISCHARGE SIZE |  |  | Φ4×Φ6×2m | [6 empty] | CHECK BALL |  | CERAMIC
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL GUIDE |  | PVDF
21 | CONTROLS | [9 empty] | BALL SEAT |  | FKM(ETP)
22 | TYPE |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | JOINT |  | PVDF
23 | ADJUST. METHOD |  |  | STROKE SPEED | [6 empty] | O-RING |  | FKM(ETP)
24 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | SPRING(VALVE) |  | NONE
25 | [10 empty] | HOSE (DIS./SUC.) |  | PTFE / PTFE
26 | SIGNAL | [9 empty] | DRIVE (SOLENOID)
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | INSULATION CLASS |  | F
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE RUN/STOP INPUT | [5 empty] | PROTECTION CLASS |  | IP65
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | WEIGHT |  |  | 2.5 | [5 empty] | kg | CABLE SIZE |  | 3C×0.75SQ×2m
34 | COLOR | [9 empty] | POWER PLUG |  | EUROPE 16A 250V
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | SPARE PAERTS
36 | ACCESSORIES | [9 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | CHECK BALL |  | □ | O-RING
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH |  |  |  | □ | SPRING(VALVE)
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.

## SP-C70(수동)
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-C70-PFC-3WS-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 75 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 9 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 70 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | METARIALS
17 | FEED NUMBER |  |  | SINGLE |  |  |  | HEAD |  | PP
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | DIAPHRAGM |  | PTFE
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | CHECK BALL |  | CERAMIC
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL GUIDE |  | PP
21 | SUCTION SIZE |  |  | Φ6×Φ8×1m |  |  |  | BALL SEAT |  | FKM
22 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m |  |  |  | JOINT |  | PP
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | O-RING |  | FKM
24 | CONTROLS | [6 empty] | SPRING(VALVE) |  | NONE
25 | TYPE |  |  | MANUAL |  |  |  | HOSE (DIS./SUC.) |  | PE / PVC
26 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | DRIVE (SOLENOID)
27 | ADJUST. RANGE |  |  | 1~100% |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | [7 empty] | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | [7 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | WEIGHT |  |  | 2.4 |  |  | kg | INSULATION CLASS |  | F
31 | COLOR | [6 empty] | PROTECTION CLASS |  | IP65
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
34 | SPARE PAERTS | [6 empty] | POWER PLUG |  | NONE
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ACCESSORIES
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
37 | □ | SPRING(VALVE) | [5 empty] | ■ | STRAINER FOOT V/V
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-C70-PFC-3WS-111
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 75 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 9 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 70 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | METARIALS
17 | FEED NUMBER |  |  | SINGLE |  |  |  | HEAD |  | PP
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | DIAPHRAGM |  | PTFE
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | CHECK BALL |  | CERAMIC
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL GUIDE |  | PP
21 | SUCTION SIZE |  |  | Φ6×Φ8×1m |  |  |  | BALL SEAT |  | FKM
22 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m |  |  |  | JOINT |  | PP
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | O-RING |  | FKM
24 | CONTROLS | [6 empty] | SPRING(VALVE) |  | NONE
25 | TYPE |  |  | MANUAL |  |  |  | HOSE (DIS./SUC.) |  | PE / PVC
26 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | DRIVE (SOLENOID)
27 | ADJUST. RANGE |  |  | 1~100% |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | [7 empty] | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | [7 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | WEIGHT |  |  | 2.4 |  |  | kg | INSULATION CLASS |  | F
31 | COLOR | [6 empty] | PROTECTION CLASS |  | IP65
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
34 | SPARE PAERTS | [6 empty] | POWER PLUG |  | EUROPE 16A 250V
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ACCESSORIES
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
37 | □ | SPRING(VALVE) | [5 empty] | ■ | STRAINER FOOT V/V
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-C70-PFC-3WF-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 75 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 9 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | 8 ±10% |  |  | bar
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 70 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | METARIALS
17 | FEED NUMBER |  |  | SINGLE |  |  |  | HEAD |  | PP
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | DIAPHRAGM |  | PTFE
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | CHECK BALL |  | CERAMIC
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL GUIDE |  | PP
21 | SUCTION SIZE |  |  | Φ6×Φ8×1m |  |  |  | BALL SEAT |  | FKM
22 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m |  |  |  | JOINT |  | PP
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | O-RING |  | FKM
24 | CONTROLS | [6 empty] | SPRING(VALVE) |  | NONE
25 | TYPE |  |  | MANUAL |  |  |  | HOSE (DIS./SUC.) |  | PE / PVC
26 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | DRIVE (SOLENOID)
27 | ADJUST. RANGE |  |  | 1~100% |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | [7 empty] | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | [7 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | WEIGHT |  |  | 2.4 |  |  | kg | INSULATION CLASS |  | F
31 | COLOR | [6 empty] | PROTECTION CLASS |  | IP65
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
34 | SPARE PAERTS | [6 empty] | POWER PLUG |  | NONE
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ACCESSORIES
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
37 | □ | SPRING(VALVE) | [5 empty] | ■ | STRAINER FOOT V/V
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-C70-PFC-3VS-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 75 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 9 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 700 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | METARIALS
17 | FEED NUMBER |  |  | SINGLE |  |  |  | HEAD |  | PP
18 | VALVE TYPE |  |  | CHECK BALL(SPRING LOADED) |  |  |  | DIAPHRAGM |  | PTFE
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | CHECK BALL |  | CERAMIC
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL GUIDE |  | PP
21 | SUCTION SIZE |  |  | Φ6×Φ8×1m |  |  |  | BALL SEAT |  | FKM
22 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m |  |  |  | JOINT |  | PP
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | O-RING |  | FKM
24 | CONTROLS | [6 empty] | SPRING(VALVE) |  | STS304
25 | TYPE |  |  | MANUAL |  |  |  | HOSE (DIS./SUC.) |  | PE / PVC
26 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | DRIVE (SOLENOID)
27 | ADJUST. RANGE |  |  | 1~100% |  |  |  | POWER CONSUMPTION |  | 17 (AVE.) |  |  | W
28 | [7 empty] | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | [7 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | WEIGHT |  |  | 2.4 |  |  | kg | INSULATION CLASS |  | F
31 | COLOR | [6 empty] | PROTECTION CLASS |  | IP65
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
34 | SPARE PAERTS | [6 empty] | POWER PLUG |  | NONE
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ACCESSORIES
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
37 | □ | SPRING(VALVE) | [5 empty] | ■ | STRAINER FOOT V/V
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-C70-PFC-4WS-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 75 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 9 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 70 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | METARIALS
17 | FEED NUMBER |  |  | SINGLE |  |  |  | HEAD |  | PP
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | DIAPHRAGM |  | PTFE
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | CHECK BALL |  | CERAMIC
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL GUIDE |  | PP
21 | SUCTION SIZE |  |  | Φ6×Φ11×1m |  |  |  | BALL SEAT |  | FKM
22 | DISCHARGE SIZE |  |  | Φ6×Φ11×2m |  |  |  | JOINT |  | PP
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | O-RING |  | FKM
24 | CONTROLS | [6 empty] | SPRING(VALVE) |  | NONE
25 | TYPE |  |  | MANUAL |  |  |  | HOSE (DIS./SUC.) |  | PVC(BRAIDED) / PVC(BRAIDED)
26 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | DRIVE (SOLENOID)
27 | ADJUST. RANGE |  |  | 1~100% |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | [7 empty] | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | [7 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | WEIGHT |  |  | 2.4 |  |  | kg | INSULATION CLASS |  | F
31 | COLOR | [6 empty] | PROTECTION CLASS |  | IP65
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
34 | SPARE PAERTS | [6 empty] | POWER PLUG |  | NONE
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ACCESSORIES
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
37 | □ | SPRING(VALVE) | [5 empty] | ■ | STRAINER FOOT V/V
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-C70-PFC-5WS-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 75 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 9 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 70 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | METARIALS
17 | FEED NUMBER |  |  | SINGLE |  |  |  | HEAD |  | PP
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | DIAPHRAGM |  | PTFE
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | CHECK BALL |  | CERAMIC
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL GUIDE |  | PP
21 | SUCTION SIZE |  |  | Φ5×Φ8×1m |  |  |  | BALL SEAT |  | FKM
22 | DISCHARGE SIZE |  |  | Φ5×Φ8×2m |  |  |  | JOINT |  | PP
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | O-RING |  | FKM
24 | CONTROLS | [6 empty] | SPRING(VALVE) |  | NONE
25 | TYPE |  |  | MANUAL |  |  |  | HOSE (DIS./SUC.) |  | PE / PVC
26 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | DRIVE (SOLENOID)
27 | ADJUST. RANGE |  |  | 1~100% |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | [7 empty] | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | [7 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | WEIGHT |  |  | 2.4 |  |  | kg | INSULATION CLASS |  | F
31 | COLOR | [6 empty] | PROTECTION CLASS |  | IP65
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
34 | SPARE PAERTS | [6 empty] | POWER PLUG |  | NONE
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ACCESSORIES
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
37 | □ | SPRING(VALVE) | [5 empty] | ■ | STRAINER FOOT V/V
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-C70-PEC-3WS-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 75 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 9 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 70 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | METARIALS
17 | FEED NUMBER |  |  | SINGLE |  |  |  | HEAD |  | PP
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | DIAPHRAGM |  | PTFE
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | CHECK BALL |  | CERAMIC
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL GUIDE |  | PP
21 | SUCTION SIZE |  |  | Φ6×Φ8×1m |  |  |  | BALL SEAT |  | EPDM
22 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m |  |  |  | JOINT |  | PP
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | O-RING |  | EPDM
24 | CONTROLS | [6 empty] | SPRING(VALVE) |  | NONE
25 | TYPE |  |  | MANUAL |  |  |  | HOSE (DIS./SUC.) |  | PE / PVC
26 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | DRIVE (SOLENOID)
27 | ADJUST. RANGE |  |  | 1~100% |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | [7 empty] | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | [7 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | WEIGHT |  |  | 2.4 |  |  | kg | INSULATION CLASS |  | F
31 | COLOR | [6 empty] | PROTECTION CLASS |  | IP65
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
34 | SPARE PAERTS | [6 empty] | POWER PLUG |  | NONE
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ACCESSORIES
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
37 | □ | SPRING(VALVE) | [5 empty] | ■ | STRAINER FOOT V/V
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-C70-FVC-3WS-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 75 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 9 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 70 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | METARIALS
17 | FEED NUMBER |  |  | SINGLE |  |  |  | HEAD |  | PVDF
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | DIAPHRAGM |  | PTFE
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | CHECK BALL |  | CERAMIC
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL GUIDE |  | PVDF
21 | SUCTION SIZE |  |  | Φ6×Φ8×1m |  |  |  | BALL SEAT |  | FKM(ETP)
22 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m |  |  |  | JOINT |  | PVDF
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | O-RING |  | FKM(ETP)
24 | CONTROLS | [6 empty] | SPRING(VALVE) |  | NONE
25 | TYPE |  |  | MANUAL |  |  |  | HOSE (DIS./SUC.) |  | PTFE / PTFE
26 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | DRIVE (SOLENOID)
27 | ADJUST. RANGE |  |  | 1~100% |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | [7 empty] | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | [7 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | WEIGHT |  |  | 2.5 |  |  | kg | INSULATION CLASS |  | F
31 | COLOR | [6 empty] | PROTECTION CLASS |  | IP65
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
34 | SPARE PAERTS | [6 empty] | POWER PLUG |  | NONE
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ACCESSORIES
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
37 | □ | SPRING(VALVE) | [5 empty] | ■ | STRAINER FOOT V/V
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-C70-FVC-3WS-111
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 75 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 9 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 70 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | METARIALS
17 | FEED NUMBER |  |  | SINGLE |  |  |  | HEAD |  | PVDF
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | DIAPHRAGM |  | PTFE
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | CHECK BALL |  | CERAMIC
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL GUIDE |  | PVDF
21 | SUCTION SIZE |  |  | Φ6×Φ8×1m |  |  |  | BALL SEAT |  | FKM(ETP)
22 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m |  |  |  | JOINT |  | PVDF
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | O-RING |  | FKM(ETP)
24 | CONTROLS | [6 empty] | SPRING(VALVE) |  | NONE
25 | TYPE |  |  | MANUAL |  |  |  | HOSE (DIS./SUC.) |  | PTFE / PTFE
26 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | DRIVE (SOLENOID)
27 | ADJUST. RANGE |  |  | 1~100% |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | [7 empty] | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | [7 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | WEIGHT |  |  | 2.5 |  |  | kg | INSULATION CLASS |  | F
31 | COLOR | [6 empty] | PROTECTION CLASS |  | IP65
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
34 | SPARE PAERTS | [6 empty] | POWER PLUG |  | EUROPE 16A 250V
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ACCESSORIES
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
37 | □ | SPRING(VALVE) | [5 empty] | ■ | STRAINER FOOT V/V
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.

## SP-C70(자동)
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-C700-PFC-3WS-310
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 75 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 9 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 70 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | METARIALS
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | HEAD |  | PP
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | DIAPHRAGM |  | PTFE
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | CHECK BALL |  | CERAMIC
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL GUIDE |  | PP
21 | CONTROLS | [9 empty] | BALL SEAT |  | FKM
22 | TYPE |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | JOINT |  | PP
23 | ADJUST. METHOD |  |  | STROKE SPEED | [6 empty] | O-RING |  | FKM
24 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | SPRING(VALVE) |  | NONE
25 | [10 empty] | HOSE (DIS./SUC.) |  | PE / PVC
26 | SIGNAL | [9 empty] | DRIVE (SOLENOID)
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | INSULATION CLASS |  | F
31 | ■ | LEVEL S/W INPUT |  | □ | REMOTE START/STOP INPUT | [5 empty] | PROTECTION CLASS |  | IP65
32 | □ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | WEIGHT |  |  | 2.4 | [5 empty] | kg | CABLE SIZE |  | 3C×0.75SQ×2m
34 | COLOR | [9 empty] | POWER PLUG |  | NONE
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | SPARE PAERTS
36 | ACCESSORIES | [9 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | CHECK BALL |  | □ | O-RING
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH |  |  |  | □ | SPRING(VALVE)
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-C70-PFC-3WS-410
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 75 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 9 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 70 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | METARIALS
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | HEAD |  | PP
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | DIAPHRAGM |  | PTFE
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | CHECK BALL |  | CERAMIC
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL GUIDE |  | PP
21 | CONTROLS | [9 empty] | BALL SEAT |  | FKM
22 | TYPE |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | JOINT |  | PP
23 | ADJUST. METHOD |  |  | STROKE SPEED | [6 empty] | O-RING |  | FKM
24 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | SPRING(VALVE) |  | NONE
25 | [10 empty] | HOSE (DIS./SUC.) |  | PE / PVC
26 | SIGNAL | [9 empty] | DRIVE (SOLENOID)
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | INSULATION CLASS |  | F
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE RUN/STOP INPUT | [5 empty] | PROTECTION CLASS |  | IP65
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | WEIGHT |  |  | 2.4 | [5 empty] | kg | CABLE SIZE |  | 3C×0.75SQ×2m
34 | COLOR | [9 empty] | POWER PLUG |  | NONE
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | SPARE PAERTS
36 | ACCESSORIES | [9 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | CHECK BALL |  | □ | O-RING
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH |  |  |  | □ | SPRING(VALVE)
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-C70-PFC-3WS-311
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 75 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 9 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 70 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | METARIALS
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | HEAD |  | PP
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | DIAPHRAGM |  | PTFE
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | CHECK BALL |  | CERAMIC
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL GUIDE |  | PP
21 | CONTROLS | [9 empty] | BALL SEAT |  | FKM
22 | TYPE |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | JOINT |  | PP
23 | ADJUST. METHOD |  |  | STROKE SPEED | [6 empty] | O-RING |  | FKM
24 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | SPRING(VALVE) |  | NONE
25 | [10 empty] | HOSE (DIS./SUC.) |  | PE / PVC
26 | SIGNAL | [9 empty] | DRIVE (SOLENOID)
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | INSULATION CLASS |  | F
31 | ■ | LEVEL S/W INPUT |  | □ | REMOTE START/STOP INPUT | [5 empty] | PROTECTION CLASS |  | IP65
32 | □ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | WEIGHT |  |  | 2.5 | [5 empty] | kg | CABLE SIZE |  | 3C×0.75SQ×2m
34 | COLOR | [9 empty] | POWER PLUG |  | EUROPE 16A 250V
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | SPARE PAERTS
36 | ACCESSORIES | [9 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | CHECK BALL |  | □ | O-RING
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH |  |  |  | □ | SPRING(VALVE)
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-C70-PFC-3WS-411
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 75 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 9 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 70 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | METARIALS
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | HEAD |  | PP
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | DIAPHRAGM |  | PTFE
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | CHECK BALL |  | CERAMIC
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL GUIDE |  | PP
21 | CONTROLS | [9 empty] | BALL SEAT |  | FKM
22 | TYPE |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | JOINT |  | PP
23 | ADJUST. METHOD |  |  | STROKE SPEED | [6 empty] | O-RING |  | FKM
24 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | SPRING(VALVE) |  | NONE
25 | [10 empty] | HOSE (DIS./SUC.) |  | PE / PVC
26 | SIGNAL | [9 empty] | DRIVE (SOLENOID)
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | INSULATION CLASS |  | F
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE RUN/STOP INPUT | [5 empty] | PROTECTION CLASS |  | IP65
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | WEIGHT |  |  | 2.5 | [5 empty] | kg | CABLE SIZE |  | 3C×0.75SQ×2m
34 | COLOR | [9 empty] | POWER PLUG |  | EUROPE 16A 250V
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | SPARE PAERTS
36 | ACCESSORIES | [9 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | CHECK BALL |  | □ | O-RING
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH |  |  |  | □ | SPRING(VALVE)
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-C700-FVC-3WS-310
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 75 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 9 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 70 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | METARIALS
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | HEAD |  | PVDF
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | DIAPHRAGM |  | PTFE
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | CHECK BALL |  | CERAMIC
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL GUIDE |  | PVDF
21 | CONTROLS | [9 empty] | BALL SEAT |  | FKM(ETP)
22 | TYPE |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | JOINT |  | PVDF
23 | ADJUST. METHOD |  |  | STROKE SPEED | [6 empty] | O-RING |  | FKM(ETP)
24 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | SPRING(VALVE) |  | NONE
25 | [10 empty] | HOSE (DIS./SUC.) |  | PTFE / PTFE
26 | SIGNAL | [9 empty] | DRIVE (SOLENOID)
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | INSULATION CLASS |  | F
31 | ■ | LEVEL S/W INPUT |  | □ | REMOTE START/STOP INPUT | [5 empty] | PROTECTION CLASS |  | IP65
32 | □ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | WEIGHT |  |  | 2.5 | [5 empty] | kg | CABLE SIZE |  | 3C×0.75SQ×2m
34 | COLOR | [9 empty] | POWER PLUG |  | NONE
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | SPARE PAERTS
36 | ACCESSORIES | [9 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | CHECK BALL |  | □ | O-RING
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH |  |  |  | □ | SPRING(VALVE)
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-C70-FVC-3WS-410
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 75 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 9 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 70 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | METARIALS
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | HEAD |  | PVDF
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | DIAPHRAGM |  | PTFE
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | CHECK BALL |  | CERAMIC
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL GUIDE |  | PVDF
21 | CONTROLS | [9 empty] | BALL SEAT |  | FKM(ETP)
22 | TYPE |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | JOINT |  | PVDF
23 | ADJUST. METHOD |  |  | STROKE SPEED | [6 empty] | O-RING |  | FKM(ETP)
24 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | SPRING(VALVE) |  | NONE
25 | [10 empty] | HOSE (DIS./SUC.) |  | PTFE / PTFE
26 | SIGNAL | [9 empty] | DRIVE (SOLENOID)
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | INSULATION CLASS |  | F
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE RUN/STOP INPUT | [5 empty] | PROTECTION CLASS |  | IP65
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | WEIGHT |  |  | 2.5 | [5 empty] | kg | CABLE SIZE |  | 3C×0.75SQ×2m
34 | COLOR | [9 empty] | POWER PLUG |  | NONE
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | SPARE PAERTS
36 | ACCESSORIES | [9 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | CHECK BALL |  | □ | O-RING
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH |  |  |  | □ | SPRING(VALVE)
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-C70-FVC-3WS-311
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 75 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 9 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 70 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | METARIALS
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | HEAD |  | PVDF
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | DIAPHRAGM |  | PTFE
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | CHECK BALL |  | CERAMIC
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL GUIDE |  | PVDF
21 | CONTROLS | [9 empty] | BALL SEAT |  | FKM(ETP)
22 | TYPE |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | JOINT |  | PVDF
23 | ADJUST. METHOD |  |  | STROKE SPEED | [6 empty] | O-RING |  | FKM(ETP)
24 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | SPRING(VALVE) |  | NONE
25 | [10 empty] | HOSE (DIS./SUC.) |  | PTFE / PTFE
26 | SIGNAL | [9 empty] | DRIVE (SOLENOID)
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | INSULATION CLASS |  | F
31 | ■ | LEVEL S/W INPUT |  | □ | REMOTE START/STOP INPUT | [5 empty] | PROTECTION CLASS |  | IP65
32 | □ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | WEIGHT |  |  | 2.6 | [5 empty] | kg | CABLE SIZE |  | 3C×0.75SQ×2m
34 | COLOR | [9 empty] | POWER PLUG |  | EUROPE 16A 250V
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | SPARE PAERTS
36 | ACCESSORIES | [9 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | CHECK BALL |  | □ | O-RING
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH |  |  |  | □ | SPRING(VALVE)
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-C70-FVC-3WS-411
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 75 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 9 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 70 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | METARIALS
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | HEAD |  | PVDF
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | DIAPHRAGM |  | PTFE
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | CHECK BALL |  | CERAMIC
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL GUIDE |  | PVDF
21 | CONTROLS | [9 empty] | BALL SEAT |  | FKM(ETP)
22 | TYPE |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | JOINT |  | PVDF
23 | ADJUST. METHOD |  |  | STROKE SPEED | [6 empty] | O-RING |  | FKM(ETP)
24 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | SPRING(VALVE) |  | NONE
25 | [10 empty] | HOSE (DIS./SUC.) |  | PTFE / PTFE
26 | SIGNAL | [9 empty] | DRIVE (SOLENOID)
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | INSULATION CLASS |  | F
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE RUN/STOP INPUT | [5 empty] | PROTECTION CLASS |  | IP65
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | WEIGHT |  |  | 2.6 | [5 empty] | kg | CABLE SIZE |  | 3C×0.75SQ×2m
34 | COLOR | [9 empty] | POWER PLUG |  | EUROPE 16A 250V
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | SPARE PAERTS
36 | ACCESSORIES | [9 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | CHECK BALL |  | □ | O-RING
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH |  |  |  | □ | SPRING(VALVE)
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.

## SP-C100(수동)
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-C100-PFC-3WS-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 140 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 5.5 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 70 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | METARIALS
17 | FEED NUMBER |  |  | SINGLE |  |  |  | HEAD |  | PP
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | DIAPHRAGM |  | PTFE
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | CHECK BALL |  | CERAMIC
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL GUIDE |  | PP
21 | SUCTION SIZE |  |  | Φ6×Φ8×1m |  |  |  | BALL SEAT |  | FKM
22 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m |  |  |  | JOINT |  | PP
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | O-RING |  | FKM
24 | CONTROLS | [6 empty] | SPRING(VALVE) |  | NONE
25 | TYPE |  |  | MANUAL |  |  |  | HOSE (DIS./SUC.) |  | PE / PVC
26 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | DRIVE (SOLENOID)
27 | ADJUST. RANGE |  |  | 1~100% |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | [7 empty] | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | [7 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | WEIGHT |  |  | 2.4 |  |  | kg | INSULATION CLASS |  | F
31 | COLOR | [6 empty] | PROTECTION CLASS |  | IP65
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
34 | SPARE PAERTS | [6 empty] | POWER PLUG |  | NONE
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ACCESSORIES
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
37 | □ | SPRING(VALVE) | [5 empty] | ■ | STRAINER FOOT V/V
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-C100-PFC-3WS-111
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 140 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 5.5 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 70 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | METARIALS
17 | FEED NUMBER |  |  | SINGLE |  |  |  | HEAD |  | PP
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | DIAPHRAGM |  | PTFE
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | CHECK BALL |  | CERAMIC
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL GUIDE |  | PP
21 | SUCTION SIZE |  |  | Φ6×Φ8×1m |  |  |  | BALL SEAT |  | FKM
22 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m |  |  |  | JOINT |  | PP
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | O-RING |  | FKM
24 | CONTROLS | [6 empty] | SPRING(VALVE) |  | NONE
25 | TYPE |  |  | MANUAL |  |  |  | HOSE (DIS./SUC.) |  | PE / PVC
26 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | DRIVE (SOLENOID)
27 | ADJUST. RANGE |  |  | 1~100% |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | [7 empty] | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | [7 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | WEIGHT |  |  | 2.5 |  |  | kg | INSULATION CLASS |  | F
31 | COLOR | [6 empty] | PROTECTION CLASS |  | IP65
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
34 | SPARE PAERTS | [6 empty] | POWER PLUG |  | EUROPE 16A 250V
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ACCESSORIES
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
37 | □ | SPRING(VALVE) | [5 empty] | ■ | STRAINER FOOT V/V
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-C100-PFC-3WF-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 140 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 5.5 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | 5 ±10% |  |  | bar
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 70 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | METARIALS
17 | FEED NUMBER |  |  | SINGLE |  |  |  | HEAD |  | PP
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | DIAPHRAGM |  | PTFE
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | CHECK BALL |  | CERAMIC
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL GUIDE |  | PP
21 | SUCTION SIZE |  |  | Φ6×Φ8×1m |  |  |  | BALL SEAT |  | FKM
22 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m |  |  |  | JOINT |  | PP
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | O-RING |  | FKM
24 | CONTROLS | [6 empty] | SPRING(VALVE) |  | NONE
25 | TYPE |  |  | MANUAL |  |  |  | HOSE (DIS./SUC.) |  | PE / PVC
26 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | DRIVE (SOLENOID)
27 | ADJUST. RANGE |  |  | 1~100% |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | [7 empty] | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | [7 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | WEIGHT |  |  | 2.4 |  |  | kg | INSULATION CLASS |  | F
31 | COLOR | [6 empty] | PROTECTION CLASS |  | IP65
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
34 | SPARE PAERTS | [6 empty] | POWER PLUG |  | NONE
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ACCESSORIES
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
37 | □ | SPRING(VALVE) | [5 empty] | ■ | STRAINER FOOT V/V
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-C100-PFC-3VS-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 140 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 5.5 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 600 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | METARIALS
17 | FEED NUMBER |  |  | SINGLE |  |  |  | HEAD |  | PP
18 | VALVE TYPE |  |  | CHECK BALL(SPRING LOADED) |  |  |  | DIAPHRAGM |  | PTFE
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | CHECK BALL |  | CERAMIC
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL GUIDE |  | PP
21 | SUCTION SIZE |  |  | Φ6×Φ8×1m |  |  |  | BALL SEAT |  | FKM
22 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m |  |  |  | JOINT |  | PP
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | O-RING |  | FKM
24 | CONTROLS | [6 empty] | SPRING(VALVE) |  | STS304
25 | TYPE |  |  | MANUAL |  |  |  | HOSE (DIS./SUC.) |  | PE / PVC
26 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | DRIVE (SOLENOID)
27 | ADJUST. RANGE |  |  | 1~100% |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | [7 empty] | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | [7 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | WEIGHT |  |  | 2.4 |  |  | kg | INSULATION CLASS |  | F
31 | COLOR | [6 empty] | PROTECTION CLASS |  | IP65
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
34 | SPARE PAERTS | [6 empty] | POWER PLUG |  | NONE
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ACCESSORIES
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
37 | □ | SPRING(VALVE) | [5 empty] | ■ | STRAINER FOOT V/V
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-C100-PFC-4WS-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 140 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 5.5 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 70 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | METARIALS
17 | FEED NUMBER |  |  | SINGLE |  |  |  | HEAD |  | PP
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | DIAPHRAGM |  | PTFE
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | CHECK BALL |  | CERAMIC
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL GUIDE |  | PP
21 | SUCTION SIZE |  |  | Φ6×Φ11×1m |  |  |  | BALL SEAT |  | FKM
22 | DISCHARGE SIZE |  |  | Φ6×Φ11×2m |  |  |  | JOINT |  | PP
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | O-RING |  | FKM
24 | CONTROLS | [6 empty] | SPRING(VALVE) |  | NONE
25 | TYPE |  |  | MANUAL |  |  |  | HOSE (DIS./SUC.) |  | PVC(BRAIDED) / PVC(BRAIDED)
26 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | DRIVE (SOLENOID)
27 | ADJUST. RANGE |  |  | 1~100% |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | [7 empty] | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | [7 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | WEIGHT |  |  | 2.4 |  |  | kg | INSULATION CLASS |  | F
31 | COLOR | [6 empty] | PROTECTION CLASS |  | IP65
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
34 | SPARE PAERTS | [6 empty] | POWER PLUG |  | NONE
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ACCESSORIES
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
37 | □ | SPRING(VALVE) | [5 empty] | ■ | STRAINER FOOT V/V
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-C100-PFC-5WS-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 140 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 5.5 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 70 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | METARIALS
17 | FEED NUMBER |  |  | SINGLE |  |  |  | HEAD |  | PP
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | DIAPHRAGM |  | PTFE
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | CHECK BALL |  | CERAMIC
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL GUIDE |  | PP
21 | SUCTION SIZE |  |  | Φ5×Φ8×1m |  |  |  | BALL SEAT |  | FKM
22 | DISCHARGE SIZE |  |  | Φ5×Φ8×2m |  |  |  | JOINT |  | PP
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | O-RING |  | FKM
24 | CONTROLS | [6 empty] | SPRING(VALVE) |  | NONE
25 | TYPE |  |  | MANUAL |  |  |  | HOSE (DIS./SUC.) |  | PE / PVC
26 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | DRIVE (SOLENOID)
27 | ADJUST. RANGE |  |  | 1~100% |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | [7 empty] | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | [7 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | WEIGHT |  |  | 2.4 |  |  | kg | INSULATION CLASS |  | F
31 | COLOR | [6 empty] | PROTECTION CLASS |  | IP65
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
34 | SPARE PAERTS | [6 empty] | POWER PLUG |  | NONE
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ACCESSORIES
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
37 | □ | SPRING(VALVE) | [5 empty] | ■ | STRAINER FOOT V/V
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-C100-PEC-3WS-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 140 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 5.5 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 70 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | METARIALS
17 | FEED NUMBER |  |  | SINGLE |  |  |  | HEAD |  | PP
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | DIAPHRAGM |  | PTFE
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | CHECK BALL |  | CERAMIC
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL GUIDE |  | PP
21 | SUCTION SIZE |  |  | Φ6×Φ8×1m |  |  |  | BALL SEAT |  | EPDM
22 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m |  |  |  | JOINT |  | PP
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | O-RING |  | EPDM
24 | CONTROLS | [6 empty] | SPRING(VALVE) |  | NONE
25 | TYPE |  |  | MANUAL |  |  |  | HOSE (DIS./SUC.) |  | PE / PVC
26 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | DRIVE (SOLENOID)
27 | ADJUST. RANGE |  |  | 1~100% |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | [7 empty] | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | [7 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | WEIGHT |  |  | 2.4 |  |  | kg | INSULATION CLASS |  | F
31 | COLOR | [6 empty] | PROTECTION CLASS |  | IP65
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
34 | SPARE PAERTS | [6 empty] | POWER PLUG |  | NONE
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ACCESSORIES
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
37 | □ | SPRING(VALVE) | [5 empty] | ■ | STRAINER FOOT V/V
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-C100-FVC-3WS-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 140 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 5.5 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 70 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | METARIALS
17 | FEED NUMBER |  |  | SINGLE |  |  |  | HEAD |  | PVDF
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | DIAPHRAGM |  | PTFE
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | CHECK BALL |  | CERAMIC
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL GUIDE |  | PVDF
21 | SUCTION SIZE |  |  | Φ6×Φ8×1m |  |  |  | BALL SEAT |  | FKM(ETP)
22 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m |  |  |  | JOINT |  | PVDF
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | O-RING |  | FKM(ETP)
24 | CONTROLS | [6 empty] | SPRING(VALVE) |  | NONE
25 | TYPE |  |  | MANUAL |  |  |  | HOSE (DIS./SUC.) |  | PTFE / PTFE
26 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | DRIVE (SOLENOID)
27 | ADJUST. RANGE |  |  | 1~100% |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | [7 empty] | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | [7 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | WEIGHT |  |  | 2.5 |  |  | kg | INSULATION CLASS |  | F
31 | COLOR | [6 empty] | PROTECTION CLASS |  | IP65
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
34 | SPARE PAERTS | [6 empty] | POWER PLUG |  | NONE
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ACCESSORIES
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
37 | □ | SPRING(VALVE) | [5 empty] | ■ | STRAINER FOOT V/V
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-C100-FVC-3WS-111
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 140 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 5.5 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 70 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | METARIALS
17 | FEED NUMBER |  |  | SINGLE |  |  |  | HEAD |  | PVDF
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | DIAPHRAGM |  | PTFE
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | CHECK BALL |  | CERAMIC
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL GUIDE |  | PVDF
21 | SUCTION SIZE |  |  | Φ6×Φ8×1m |  |  |  | BALL SEAT |  | FKM(ETP)
22 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m |  |  |  | JOINT |  | PVDF
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | O-RING |  | FKM(ETP)
24 | CONTROLS | [6 empty] | SPRING(VALVE) |  | NONE
25 | TYPE |  |  | MANUAL |  |  |  | HOSE (DIS./SUC.) |  | PTFE / PTFE
26 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | DRIVE (SOLENOID)
27 | ADJUST. RANGE |  |  | 1~100% |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | [7 empty] | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | [7 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | WEIGHT |  |  | 2.6 |  |  | kg | INSULATION CLASS |  | F
31 | COLOR | [6 empty] | PROTECTION CLASS |  | IP65
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
34 | SPARE PAERTS | [6 empty] | POWER PLUG |  | EUROPE 16A 250V
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ACCESSORIES
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
37 | □ | SPRING(VALVE) | [5 empty] | ■ | STRAINER FOOT V/V
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.

## SP-C100(자동)
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-C100-PFC-3WS-310
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 140 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 5.5 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 70 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | METARIALS
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | HEAD |  | PP
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | DIAPHRAGM |  | PTFE
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | CHECK BALL |  | CERAMIC
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL GUIDE |  | PP
21 | CONTROLS | [9 empty] | BALL SEAT |  | FKM
22 | TYPE |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | JOINT |  | PP
23 | ADJUST. METHOD |  |  | STROKE SPEED | [6 empty] | O-RING |  | FKM
24 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | SPRING(VALVE) |  | NONE
25 | [10 empty] | HOSE (DIS./SUC.) |  | PE / PVC
26 | SIGNAL | [9 empty] | DRIVE (SOLENOID)
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | INSULATION CLASS |  | F
31 | ■ | LEVEL S/W INPUT |  | □ | REMOTE START/STOP INPUT | [5 empty] | PROTECTION CLASS |  | IP65
32 | □ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | WEIGHT |  |  | 2.5 | [5 empty] | kg | CABLE SIZE |  | 3C×0.75SQ×2m
34 | COLOR | [9 empty] | POWER PLUG |  | NONE
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | SPARE PAERTS
36 | ACCESSORIES | [9 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | CHECK BALL |  | □ | O-RING
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH |  |  |  | □ | SPRING(VALVE)
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-C100-PFC-3WS-410
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 140 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 5.5 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 70 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | METARIALS
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | HEAD |  | PP
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | DIAPHRAGM |  | PTFE
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | CHECK BALL |  | CERAMIC
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL GUIDE |  | PP
21 | CONTROLS | [9 empty] | BALL SEAT |  | FKM
22 | TYPE |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | JOINT |  | PP
23 | ADJUST. METHOD |  |  | STROKE SPEED | [6 empty] | O-RING |  | FKM
24 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | SPRING(VALVE) |  | NONE
25 | [10 empty] | HOSE (DIS./SUC.) |  | PE / PVC
26 | SIGNAL | [9 empty] | DRIVE (SOLENOID)
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | INSULATION CLASS |  | F
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE RUN/STOP INPUT | [5 empty] | PROTECTION CLASS |  | IP65
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | WEIGHT |  |  | 2.5 | [5 empty] | kg | CABLE SIZE |  | 3C×0.75SQ×2m
34 | COLOR | [9 empty] | POWER PLUG |  | NONE
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | SPARE PAERTS
36 | ACCESSORIES | [9 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | CHECK BALL |  | □ | O-RING
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH |  |  |  | □ | SPRING(VALVE)
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-C100-PFC-3WS-311
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 140 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 5.5 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 70 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | METARIALS
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | HEAD |  | PP
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | DIAPHRAGM |  | PTFE
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | CHECK BALL |  | CERAMIC
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL GUIDE |  | PP
21 | CONTROLS | [9 empty] | BALL SEAT |  | FKM
22 | TYPE |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | JOINT |  | PP
23 | ADJUST. METHOD |  |  | STROKE SPEED | [6 empty] | O-RING |  | FKM
24 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | SPRING(VALVE) |  | NONE
25 | [10 empty] | HOSE (DIS./SUC.) |  | PE / PVC
26 | SIGNAL | [9 empty] | DRIVE (SOLENOID)
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | INSULATION CLASS |  | F
31 | ■ | LEVEL S/W INPUT |  | □ | REMOTE START/STOP INPUT | [5 empty] | PROTECTION CLASS |  | IP65
32 | □ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | WEIGHT |  |  | 2.6 | [5 empty] | kg | CABLE SIZE |  | 3C×0.75SQ×2m
34 | COLOR | [9 empty] | POWER PLUG |  | EUROPE 16A 250V
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | SPARE PAERTS
36 | ACCESSORIES | [9 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | CHECK BALL |  | □ | O-RING
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH |  |  |  | □ | SPRING(VALVE)
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-C100-PFC-3WS-411
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 140 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 5.5 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 70 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | METARIALS
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | HEAD |  | PP
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | DIAPHRAGM |  | PTFE
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | CHECK BALL |  | CERAMIC
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL GUIDE |  | PP
21 | CONTROLS | [9 empty] | BALL SEAT |  | FKM
22 | TYPE |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | JOINT |  | PP
23 | ADJUST. METHOD |  |  | STROKE SPEED | [6 empty] | O-RING |  | FKM
24 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | SPRING(VALVE) |  | NONE
25 | [10 empty] | HOSE (DIS./SUC.) |  | PE / PVC
26 | SIGNAL | [9 empty] | DRIVE (SOLENOID)
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | INSULATION CLASS |  | F
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE RUN/STOP INPUT | [5 empty] | PROTECTION CLASS |  | IP65
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | WEIGHT |  |  | 2.6 | [5 empty] | kg | CABLE SIZE |  | 3C×0.75SQ×2m
34 | COLOR | [9 empty] | POWER PLUG |  | EUROPE 16A 250V
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | SPARE PAERTS
36 | ACCESSORIES | [9 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | CHECK BALL |  | □ | O-RING
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH |  |  |  | □ | SPRING(VALVE)
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-C100-FVC-3WS-310
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 140 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 5.5 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 70 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | METARIALS
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | HEAD |  | PVDF
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | DIAPHRAGM |  | PTFE
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | CHECK BALL |  | CERAMIC
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL GUIDE |  | PVDF
21 | CONTROLS | [9 empty] | BALL SEAT |  | FKM(ETP)
22 | TYPE |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | JOINT |  | PVDF
23 | ADJUST. METHOD |  |  | STROKE SPEED | [6 empty] | O-RING |  | FKM(ETP)
24 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | SPRING(VALVE) |  | NONE
25 | [10 empty] | HOSE (DIS./SUC.) |  | PTFE / PTFE
26 | SIGNAL | [9 empty] | DRIVE (SOLENOID)
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | INSULATION CLASS |  | F
31 | ■ | LEVEL S/W INPUT |  | □ | REMOTE START/STOP INPUT | [5 empty] | PROTECTION CLASS |  | IP65
32 | □ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | WEIGHT |  |  | 2.6 | [5 empty] | kg | CABLE SIZE |  | 3C×0.75SQ×2m
34 | COLOR | [9 empty] | POWER PLUG |  | NONE
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | SPARE PAERTS
36 | ACCESSORIES | [9 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | CHECK BALL |  | □ | O-RING
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH |  |  |  | □ | SPRING(VALVE)
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-C100-FVC-3WS-410
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 140 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 5.5 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 70 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | METARIALS
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | HEAD |  | PVDF
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | DIAPHRAGM |  | PTFE
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | CHECK BALL |  | CERAMIC
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL GUIDE |  | PVDF
21 | CONTROLS | [9 empty] | BALL SEAT |  | FKM(ETP)
22 | TYPE |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | JOINT |  | PVDF
23 | ADJUST. METHOD |  |  | STROKE SPEED | [6 empty] | O-RING |  | FKM(ETP)
24 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | SPRING(VALVE) |  | NONE
25 | [10 empty] | HOSE (DIS./SUC.) |  | PTFE / PTFE
26 | SIGNAL | [9 empty] | DRIVE (SOLENOID)
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | INSULATION CLASS |  | F
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE RUN/STOP INPUT | [5 empty] | PROTECTION CLASS |  | IP65
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | WEIGHT |  |  | 2.6 | [5 empty] | kg | CABLE SIZE |  | 3C×0.75SQ×2m
34 | COLOR | [9 empty] | POWER PLUG |  | NONE
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | SPARE PAERTS
36 | ACCESSORIES | [9 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | CHECK BALL |  | □ | O-RING
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH |  |  |  | □ | SPRING(VALVE)
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-C100-FVC-3WS-311
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 140 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 5.5 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 70 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | METARIALS
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | HEAD |  | PVDF
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | DIAPHRAGM |  | PTFE
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | CHECK BALL |  | CERAMIC
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL GUIDE |  | PVDF
21 | CONTROLS | [9 empty] | BALL SEAT |  | FKM(ETP)
22 | TYPE |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | JOINT |  | PVDF
23 | ADJUST. METHOD |  |  | STROKE SPEED | [6 empty] | O-RING |  | FKM(ETP)
24 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | SPRING(VALVE) |  | NONE
25 | [10 empty] | HOSE (DIS./SUC.) |  | PTFE / PTFE
26 | SIGNAL | [9 empty] | DRIVE (SOLENOID)
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | INSULATION CLASS |  | F
31 | ■ | LEVEL S/W INPUT |  | □ | REMOTE START/STOP INPUT | [5 empty] | PROTECTION CLASS |  | IP65
32 | □ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | WEIGHT |  |  | 2.6 | [5 empty] | kg | CABLE SIZE |  | 3C×0.75SQ×2m
34 | COLOR | [9 empty] | POWER PLUG |  | EUROPE 16A 250V
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | SPARE PAERTS
36 | ACCESSORIES | [9 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | CHECK BALL |  | □ | O-RING
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH |  |  |  | □ | SPRING(VALVE)
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-C100-FVC-3WS-411
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 140 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 5.5 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 70 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | METARIALS
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | HEAD |  | PVDF
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | DIAPHRAGM |  | PTFE
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | CHECK BALL |  | CERAMIC
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL GUIDE |  | PVDF
21 | CONTROLS | [9 empty] | BALL SEAT |  | FKM(ETP)
22 | TYPE |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | JOINT |  | PVDF
23 | ADJUST. METHOD |  |  | STROKE SPEED | [6 empty] | O-RING |  | FKM(ETP)
24 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | SPRING(VALVE) |  | NONE
25 | [10 empty] | HOSE (DIS./SUC.) |  | PTFE / PTFE
26 | SIGNAL | [9 empty] | DRIVE (SOLENOID)
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | INSULATION CLASS |  | F
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE RUN/STOP INPUT | [5 empty] | PROTECTION CLASS |  | IP65
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | WEIGHT |  |  | 2.6 | [5 empty] | kg | CABLE SIZE |  | 3C×0.75SQ×2m
34 | COLOR | [9 empty] | POWER PLUG |  | EUROPE 16A 250V
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | SPARE PAERTS
36 | ACCESSORIES | [9 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | CHECK BALL |  | □ | O-RING
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH |  |  |  | □ | SPRING(VALVE)
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.

## SP-C200(수동)
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-C200-PFC-3WS-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 200 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 3 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 70 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | METARIALS
17 | FEED NUMBER |  |  | SINGLE |  |  |  | HEAD |  | PP
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | DIAPHRAGM |  | PTFE
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | CHECK BALL |  | CERAMIC
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL GUIDE |  | PP
21 | SUCTION SIZE |  |  | Φ6×Φ8×1m |  |  |  | BALL SEAT |  | FKM
22 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m |  |  |  | JOINT |  | PP
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | O-RING |  | FKM
24 | CONTROLS | [6 empty] | SPRING(VALVE) |  | NONE
25 | TYPE |  |  | MANUAL |  |  |  | HOSE (DIS./SUC.) |  | PE / PVC
26 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | DRIVE (SOLENOID)
27 | ADJUST. RANGE |  |  | 1~100% |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | [7 empty] | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | [7 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | WEIGHT |  |  | 2.4 |  |  | kg | INSULATION CLASS |  | F
31 | COLOR | [6 empty] | PROTECTION CLASS |  | IP65
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
34 | SPARE PAERTS | [6 empty] | POWER PLUG |  | NONE
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ACCESSORIES
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
37 | □ | SPRING(VALVE) | [5 empty] | ■ | STRAINER FOOT V/V
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-C200-PFC-3WS-111
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 200 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 3 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 70 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | METARIALS
17 | FEED NUMBER |  |  | SINGLE |  |  |  | HEAD |  | PP
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | DIAPHRAGM |  | PTFE
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | CHECK BALL |  | CERAMIC
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL GUIDE |  | PP
21 | SUCTION SIZE |  |  | Φ6×Φ8×1m |  |  |  | BALL SEAT |  | FKM
22 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m |  |  |  | JOINT |  | PP
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | O-RING |  | FKM
24 | CONTROLS | [6 empty] | SPRING(VALVE) |  | NONE
25 | TYPE |  |  | MANUAL |  |  |  | HOSE (DIS./SUC.) |  | PE / PVC
26 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | DRIVE (SOLENOID)
27 | ADJUST. RANGE |  |  | 1~100% |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | [7 empty] | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | [7 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | WEIGHT |  |  | 2.5 |  |  | kg | INSULATION CLASS |  | F
31 | COLOR | [6 empty] | PROTECTION CLASS |  | IP65
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
34 | SPARE PAERTS | [6 empty] | POWER PLUG |  | EUROPE 16A 250V
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ACCESSORIES
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
37 | □ | SPRING(VALVE) | [5 empty] | ■ | STRAINER FOOT V/V
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-C200-PFC-3VS-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 200 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 3 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 400 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | METARIALS
17 | FEED NUMBER |  |  | SINGLE |  |  |  | HEAD |  | PP
18 | VALVE TYPE |  |  | CHECK BALL(SPRING LOADED) |  |  |  | DIAPHRAGM |  | PTFE
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | CHECK BALL |  | CERAMIC
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL GUIDE |  | PP
21 | SUCTION SIZE |  |  | Φ6×Φ8×1m |  |  |  | BALL SEAT |  | FKM
22 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m |  |  |  | JOINT |  | PP
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | O-RING |  | FKM
24 | CONTROLS | [6 empty] | SPRING(VALVE) |  | STS304
25 | TYPE |  |  | MANUAL |  |  |  | HOSE (DIS./SUC.) |  | PE / PVC
26 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | DRIVE (SOLENOID)
27 | ADJUST. RANGE |  |  | 1~100% |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | [7 empty] | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | [7 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | WEIGHT |  |  | 2.4 |  |  | kg | INSULATION CLASS |  | F
31 | COLOR | [6 empty] | PROTECTION CLASS |  | IP65
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
34 | SPARE PAERTS | [6 empty] | POWER PLUG |  | NONE
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ACCESSORIES
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
37 | □ | SPRING(VALVE) | [5 empty] | ■ | STRAINER FOOT V/V
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-C200-PFC-4WS-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 200 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 3 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 70 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | METARIALS
17 | FEED NUMBER |  |  | SINGLE |  |  |  | HEAD |  | PP
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | DIAPHRAGM |  | PTFE
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | CHECK BALL |  | CERAMIC
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL GUIDE |  | PP
21 | SUCTION SIZE |  |  | Φ6×Φ11×1m |  |  |  | BALL SEAT |  | FKM
22 | DISCHARGE SIZE |  |  | Φ6×Φ11×2m |  |  |  | JOINT |  | PP
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | O-RING |  | FKM
24 | CONTROLS | [6 empty] | SPRING(VALVE) |  | NONE
25 | TYPE |  |  | MANUAL |  |  |  | HOSE (DIS./SUC.) |  | PVC(BRAIDED) / PVC(BRAIDED)
26 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | DRIVE (SOLENOID)
27 | ADJUST. RANGE |  |  | 1~100% |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | [7 empty] | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | [7 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | WEIGHT |  |  | 2.4 |  |  | kg | INSULATION CLASS |  | F
31 | COLOR | [6 empty] | PROTECTION CLASS |  | IP65
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
34 | SPARE PAERTS | [6 empty] | POWER PLUG |  | NONE
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ACCESSORIES
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
37 | □ | SPRING(VALVE) | [5 empty] | ■ | STRAINER FOOT V/V
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-C200-PFC-5WS-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 200 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 3 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 70 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | METARIALS
17 | FEED NUMBER |  |  | SINGLE |  |  |  | HEAD |  | PP
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | DIAPHRAGM |  | PTFE
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | CHECK BALL |  | CERAMIC
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL GUIDE |  | PP
21 | SUCTION SIZE |  |  | Φ5×Φ8×1m |  |  |  | BALL SEAT |  | FKM
22 | DISCHARGE SIZE |  |  | Φ5×Φ8×2m |  |  |  | JOINT |  | PP
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | O-RING |  | FKM
24 | CONTROLS | [6 empty] | SPRING(VALVE) |  | NONE
25 | TYPE |  |  | MANUAL |  |  |  | HOSE (DIS./SUC.) |  | PE / PVC
26 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | DRIVE (SOLENOID)
27 | ADJUST. RANGE |  |  | 1~100% |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | [7 empty] | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | [7 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | WEIGHT |  |  | 2.4 |  |  | kg | INSULATION CLASS |  | F
31 | COLOR | [6 empty] | PROTECTION CLASS |  | IP65
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
34 | SPARE PAERTS | [6 empty] | POWER PLUG |  | NONE
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ACCESSORIES
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
37 | □ | SPRING(VALVE) | [5 empty] | ■ | STRAINER FOOT V/V
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-C200-PEC-3WS-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 200 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 3 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 70 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | METARIALS
17 | FEED NUMBER |  |  | SINGLE |  |  |  | HEAD |  | PP
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | DIAPHRAGM |  | PTFE
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | CHECK BALL |  | CERAMIC
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL GUIDE |  | PP
21 | SUCTION SIZE |  |  | Φ6×Φ8×1m |  |  |  | BALL SEAT |  | EPDM
22 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m |  |  |  | JOINT |  | PP
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | O-RING |  | EPDM
24 | CONTROLS | [6 empty] | SPRING(VALVE) |  | NONE
25 | TYPE |  |  | MANUAL |  |  |  | HOSE (DIS./SUC.) |  | PE / PVC
26 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | DRIVE (SOLENOID)
27 | ADJUST. RANGE |  |  | 1~100% |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | [7 empty] | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | [7 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | WEIGHT |  |  | 2.4 |  |  | kg | INSULATION CLASS |  | F
31 | COLOR | [6 empty] | PROTECTION CLASS |  | IP65
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
34 | SPARE PAERTS | [6 empty] | POWER PLUG |  | NONE
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ACCESSORIES
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
37 | □ | SPRING(VALVE) | [5 empty] | ■ | STRAINER FOOT V/V
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-C200-FVC-3WS-110
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 200 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 3 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 70 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | METARIALS
17 | FEED NUMBER |  |  | SINGLE |  |  |  | HEAD |  | PVDF
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | DIAPHRAGM |  | PTFE
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | CHECK BALL |  | CERAMIC
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL GUIDE |  | PVDF
21 | SUCTION SIZE |  |  | Φ6×Φ8×1m |  |  |  | BALL SEAT |  | FKM(ETP)
22 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m |  |  |  | JOINT |  | PVDF
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | O-RING |  | FKM(ETP)
24 | CONTROLS | [6 empty] | SPRING(VALVE) |  | NONE
25 | TYPE |  |  | MANUAL |  |  |  | HOSE (DIS./SUC.) |  | PTFE / PTFE
26 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | DRIVE (SOLENOID)
27 | ADJUST. RANGE |  |  | 1~100% |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | [7 empty] | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | [7 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | WEIGHT |  |  | 2.5 |  |  | kg | INSULATION CLASS |  | F
31 | COLOR | [6 empty] | PROTECTION CLASS |  | IP65
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
34 | SPARE PAERTS | [6 empty] | POWER PLUG |  | NONE
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ACCESSORIES
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
37 | □ | SPRING(VALVE) | [5 empty] | ■ | STRAINER FOOT V/V
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [6 empty] | JOB NO.
2 | PROJECT | [6 empty] | ITEM NO.
3 | SERVICE | [6 empty] | QUANTITY
4 | OPERATION CONDITIONS | [6 empty] | PERFORMANCE
5 | LIQUID | [6 empty] | PUMP MODEL |  | SP-C200-FVC-3WS-111
6 | PUMPING TEMP. | [5 empty] | ℃ | DIS. CAPACITY |  | MAX 200 |  |  | mL/min
7 | AMBIENT TEMP. | [5 empty] | ℃ | DIS. PRESSURE |  | MAX 3 |  |  | bar
8 | SPECIFIC GRAVITY | [6 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [5 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [5 empty] | mL/min | STROKE LENGTH |  | 1 |  |  | mm
11 | DIS. PRESSURE | [5 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [5 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [5 empty] | m | VISCOSITY |  | MAX 70 |  |  | mPa·s
14 | LOCATION | [6 empty] | SELF PRIMING |  | MAX 2 |  |  | mWC
15 | CONSTRUCTION | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | PUMP TYPE |  |  | DIAPHRAGM |  |  |  | METARIALS
17 | FEED NUMBER |  |  | SINGLE |  |  |  | HEAD |  | PVDF
18 | VALVE TYPE |  |  | CHECK BALL |  |  |  | DIAPHRAGM |  | PTFE
19 | VALVE NUMBER |  |  | DOUBLE |  |  |  | CHECK BALL |  | CERAMIC
20 | CONNECTION TYPE |  |  | HOSE (TUBE) |  |  |  | BALL GUIDE |  | PVDF
21 | SUCTION SIZE |  |  | Φ6×Φ8×1m |  |  |  | BALL SEAT |  | FKM(ETP)
22 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m |  |  |  | JOINT |  | PVDF
23 | AIR VENT SIZE |  |  | Φ4×Φ6×1m |  |  |  | O-RING |  | FKM(ETP)
24 | CONTROLS | [6 empty] | SPRING(VALVE) |  | NONE
25 | TYPE |  |  | MANUAL |  |  |  | HOSE (DIS./SUC.) |  | PTFE / PTFE
26 | ADJUST. METHOD |  |  | STROKE SPEED |  |  |  | DRIVE (SOLENOID)
27 | ADJUST. RANGE |  |  | 1~100% |  |  |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | [7 empty] | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | [7 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | WEIGHT |  |  | 2.6 |  |  | kg | INSULATION CLASS |  | F
31 | COLOR | [6 empty] | PROTECTION CLASS |  | IP65
32 | PUMP HOUSING |  |  | PANTONE 3125C |  |  |  | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | CONTROL PANEL |  |  | RAL 7016 |  |  |  | CABLE SIZE |  | 3C×0.75SQ×2m
34 | SPARE PAERTS | [6 empty] | POWER PLUG |  | EUROPE 16A 250V
35 | □ | DIAPHRAGM |  |  | □ | BALL SEAT |  | ACCESSORIES
36 | □ | CHECK BALL |  |  | □ | O-RING |  | ■ | HOSE |  | ■ | SIPHON CHECK V/V
37 | □ | SPRING(VALVE) | [5 empty] | ■ | STRAINER FOOT V/V
38 | REMARKS:
39
40
CHEON SEI IND. CO., LTD.

## SP-C200(자동)
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-C200-PFC-3WS-310
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 200 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 3 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 70 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | METARIALS
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | HEAD |  | PP
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | DIAPHRAGM |  | PTFE
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | CHECK BALL |  | CERAMIC
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL GUIDE |  | PP
21 | CONTROLS | [9 empty] | BALL SEAT |  | FKM
22 | TYPE |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | JOINT |  | PP
23 | ADJUST. METHOD |  |  | STROKE SPEED | [6 empty] | O-RING |  | FKM
24 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | SPRING(VALVE) |  | NONE
25 | [10 empty] | HOSE (DIS./SUC.) |  | PE / PVC
26 | SIGNAL | [9 empty] | DRIVE (SOLENOID)
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | INSULATION CLASS |  | F
31 | ■ | LEVEL S/W INPUT |  | □ | REMOTE START/STOP INPUT | [5 empty] | PROTECTION CLASS |  | IP65
32 | □ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | WEIGHT |  |  | 2.5 | [5 empty] | kg | CABLE SIZE |  | 3C×0.75SQ×2m
34 | COLOR | [9 empty] | POWER PLUG |  | NONE
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | SPARE PAERTS
36 | ACCESSORIES | [9 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | CHECK BALL |  | □ | O-RING
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH |  |  |  | □ | SPRING(VALVE)
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-C200-PFC-3WS-410
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 200 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 3 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 70 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | METARIALS
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | HEAD |  | PP
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | DIAPHRAGM |  | PTFE
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | CHECK BALL |  | CERAMIC
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL GUIDE |  | PP
21 | CONTROLS | [9 empty] | BALL SEAT |  | FKM
22 | TYPE |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | JOINT |  | PP
23 | ADJUST. METHOD |  |  | STROKE SPEED | [6 empty] | O-RING |  | FKM
24 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | SPRING(VALVE) |  | NONE
25 | [10 empty] | HOSE (DIS./SUC.) |  | PE / PVC
26 | SIGNAL | [9 empty] | DRIVE (SOLENOID)
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | INSULATION CLASS |  | F
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE RUN/STOP INPUT | [5 empty] | PROTECTION CLASS |  | IP65
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | WEIGHT |  |  | 2.5 | [5 empty] | kg | CABLE SIZE |  | 3C×0.75SQ×2m
34 | COLOR | [9 empty] | POWER PLUG |  | NONE
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | SPARE PAERTS
36 | ACCESSORIES | [9 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | CHECK BALL |  | □ | O-RING
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH |  |  |  | □ | SPRING(VALVE)
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-C200-PFC-3WS-311
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 200 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 3 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 70 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | METARIALS
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | HEAD |  | PP
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | DIAPHRAGM |  | PTFE
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | CHECK BALL |  | CERAMIC
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL GUIDE |  | PP
21 | CONTROLS | [9 empty] | BALL SEAT |  | FKM
22 | TYPE |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | JOINT |  | PP
23 | ADJUST. METHOD |  |  | STROKE SPEED | [6 empty] | O-RING |  | FKM
24 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | SPRING(VALVE) |  | NONE
25 | [10 empty] | HOSE (DIS./SUC.) |  | PE / PVC
26 | SIGNAL | [9 empty] | DRIVE (SOLENOID)
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | INSULATION CLASS |  | F
31 | ■ | LEVEL S/W INPUT |  | □ | REMOTE START/STOP INPUT | [5 empty] | PROTECTION CLASS |  | IP65
32 | □ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | WEIGHT |  |  | 2.5 | [5 empty] | kg | CABLE SIZE |  | 3C×0.75SQ×2m
34 | COLOR | [9 empty] | POWER PLUG |  | EUROPE 16A 250V
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | SPARE PAERTS
36 | ACCESSORIES | [9 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | CHECK BALL |  | □ | O-RING
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH |  |  |  | □ | SPRING(VALVE)
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-C200-PFC-3WS-411
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 200 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 3 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 70 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | METARIALS
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | HEAD |  | PP
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | DIAPHRAGM |  | PTFE
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | CHECK BALL |  | CERAMIC
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL GUIDE |  | PP
21 | CONTROLS | [9 empty] | BALL SEAT |  | FKM
22 | TYPE |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | JOINT |  | PP
23 | ADJUST. METHOD |  |  | STROKE SPEED | [6 empty] | O-RING |  | FKM
24 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | SPRING(VALVE) |  | NONE
25 | [10 empty] | HOSE (DIS./SUC.) |  | PE / PVC
26 | SIGNAL | [9 empty] | DRIVE (SOLENOID)
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | INSULATION CLASS |  | F
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE RUN/STOP INPUT | [5 empty] | PROTECTION CLASS |  | IP65
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | WEIGHT |  |  | 2.5 | [5 empty] | kg | CABLE SIZE |  | 3C×0.75SQ×2m
34 | COLOR | [9 empty] | POWER PLUG |  | EUROPE 16A 250V
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | SPARE PAERTS
36 | ACCESSORIES | [9 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | CHECK BALL |  | □ | O-RING
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH |  |  |  | □ | SPRING(VALVE)
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-C200-FVC-3WS-310
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 200 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 3 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 70 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | METARIALS
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | HEAD |  | PVDF
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | DIAPHRAGM |  | PTFE
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | CHECK BALL |  | CERAMIC
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL GUIDE |  | PVDF
21 | CONTROLS | [9 empty] | BALL SEAT |  | FKM(ETP)
22 | TYPE |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | JOINT |  | PVDF
23 | ADJUST. METHOD |  |  | STROKE SPEED | [6 empty] | O-RING |  | FKM(ETP)
24 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | SPRING(VALVE) |  | NONE
25 | [10 empty] | HOSE (DIS./SUC.) |  | PTFE / PTFE
26 | SIGNAL | [9 empty] | DRIVE (SOLENOID)
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | INSULATION CLASS |  | F
31 | ■ | LEVEL S/W INPUT |  | □ | REMOTE START/STOP INPUT | [5 empty] | PROTECTION CLASS |  | IP65
32 | □ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | WEIGHT |  |  | 2.6 | [5 empty] | kg | CABLE SIZE |  | 3C×0.75SQ×2m
34 | COLOR | [9 empty] | POWER PLUG |  | NONE
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | SPARE PAERTS
36 | ACCESSORIES | [9 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | CHECK BALL |  | □ | O-RING
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH |  |  |  | □ | SPRING(VALVE)
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-C200-FVC-3WS-410
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 200 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 3 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 70 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | METARIALS
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | HEAD |  | PVDF
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | DIAPHRAGM |  | PTFE
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | CHECK BALL |  | CERAMIC
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL GUIDE |  | PVDF
21 | CONTROLS | [9 empty] | BALL SEAT |  | FKM(ETP)
22 | TYPE |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | JOINT |  | PVDF
23 | ADJUST. METHOD |  |  | STROKE SPEED | [6 empty] | O-RING |  | FKM(ETP)
24 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | SPRING(VALVE) |  | NONE
25 | [10 empty] | HOSE (DIS./SUC.) |  | PTFE / PTFE
26 | SIGNAL | [9 empty] | DRIVE (SOLENOID)
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | INSULATION CLASS |  | F
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE RUN/STOP INPUT | [5 empty] | PROTECTION CLASS |  | IP65
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | WEIGHT |  |  | 2.6 | [5 empty] | kg | CABLE SIZE |  | 3C×0.75SQ×2m
34 | COLOR | [9 empty] | POWER PLUG |  | NONE
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | SPARE PAERTS
36 | ACCESSORIES | [9 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | CHECK BALL |  | □ | O-RING
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH |  |  |  | □ | SPRING(VALVE)
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-C200-FVC-3WS-311
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 200 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 3 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 70 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | METARIALS
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | HEAD |  | PVDF
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | DIAPHRAGM |  | PTFE
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | CHECK BALL |  | CERAMIC
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL GUIDE |  | PVDF
21 | CONTROLS | [9 empty] | BALL SEAT |  | FKM(ETP)
22 | TYPE |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | JOINT |  | PVDF
23 | ADJUST. METHOD |  |  | STROKE SPEED | [6 empty] | O-RING |  | FKM(ETP)
24 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | SPRING(VALVE) |  | NONE
25 | [10 empty] | HOSE (DIS./SUC.) |  | PTFE / PTFE
26 | SIGNAL | [9 empty] | DRIVE (SOLENOID)
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | INSULATION CLASS |  | F
31 | ■ | LEVEL S/W INPUT |  | □ | REMOTE START/STOP INPUT | [5 empty] | PROTECTION CLASS |  | IP65
32 | □ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | WEIGHT |  |  | 2.6 | [5 empty] | kg | CABLE SIZE |  | 3C×0.75SQ×2m
34 | COLOR | [9 empty] | POWER PLUG |  | EUROPE 16A 250V
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | SPARE PAERTS
36 | ACCESSORIES | [9 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | CHECK BALL |  | □ | O-RING
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH |  |  |  | □ | SPRING(VALVE)
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.
SOLENOID METERING PUMP DATA SHEET
1 | PURCHASER | [9 empty] | JOB NO.
2 | PROJECT | [9 empty] | ITEM NO.
3 | SERVICE | [9 empty] | QUANTITY
4 | OPERATION CONDITIONS | [9 empty] | PERFORMANCE
5 | LIQUID | [9 empty] | PUMP MODEL |  | SP-C200-FVC-3WS-411
6 | PUMPING TEMP. | [8 empty] | ℃ | DIS. CAPACITY |  | MAX 200 |  |  | mL/min
7 | AMBIENT TEMP. | [8 empty] | ℃ | DIS. PRESSURE |  | MAX 3 |  |  | bar
8 | SPECIFIC GRAVITY | [9 empty] | R/V SET. PRESSURE |  | NONE
9 | VISCOSITY | [8 empty] | mPa·s | STROKE SPEED |  | MAX 240 |  |  | SPM
10 | DIS. CAPACITY | [8 empty] | mL/min | STROKE LENGTH |  | 1 |  |  | mm
11 | DIS. PRESSURE | [8 empty] | bar | PUMPING TEMP. |  | 0~50 |  |  | ℃
12 | SUC. PRESSURE | [8 empty] | bar | AMBIENT TEMP. |  | 0~40 |  |  | ℃
13 | SUCTION HEAD | [8 empty] | m | VISCOSITY |  | MAX 70 |  |  | mPa·s
14 | CONSTRUCTION | [9 empty] | SELF PRIMING |  | MAX 1.5 |  |  | mWC
15 | PUMP TYPE |  |  | DIAPHRAGM | [6 empty] | SOUND LEVEL |  | MAX 70 |  |  | dB(A)
16 | VALVE TYPE/NUMBER |  |  | CHECK BALL / DOUBLE | [6 empty] | METARIALS
17 | CONNECTION TYPE |  |  | HOSE (TUBE) | [6 empty] | HEAD |  | PVDF
18 | SUCTION SIZE |  |  | Φ6×Φ8×1m | [6 empty] | DIAPHRAGM |  | PTFE
19 | DISCHARGE SIZE |  |  | Φ6×Φ8×2m | [6 empty] | CHECK BALL |  | CERAMIC
20 | AIR VENT SIZE |  |  | Φ4×Φ6×1m | [6 empty] | BALL GUIDE |  | PVDF
21 | CONTROLS | [9 empty] | BALL SEAT |  | FKM(ETP)
22 | TYPE |  |  | ■ | MANUAL |  |  | ■ | AUTOMATIC |  | JOINT |  | PVDF
23 | ADJUST. METHOD |  |  | STROKE SPEED | [6 empty] | O-RING |  | FKM(ETP)
24 | ADJUSTMENT RANGE |  |  | 1~100% | [6 empty] | SPRING(VALVE) |  | NONE
25 | [10 empty] | HOSE (DIS./SUC.) |  | PTFE / PTFE
26 | SIGNAL | [9 empty] | DRIVE (SOLENOID)
27 | ■ | PULSE INPUT |  | ■ | 1:1 |  |  | □ | DIV/MUL |  | POWER CONSUMPTION |  | AVE 17 |  |  | W
28 | MIN. PULSE DURATION |  |  | 4 | [5 empty] | ms | VOLTAGE |  | 1Φ AC220V 50/60Hz
29 | ■ | ANALOG INPUT |  | DC 4~20mA | [6 empty] | RATED CURRENT |  | 0.5 |  |  | A
30 | INPUT RESISTANCE |  |  | 250 | [5 empty] | Ω | INSULATION CLASS |  | F
31 | ■ | LEVEL S/W INPUT |  | ■ | REMOTE RUN/STOP INPUT | [5 empty] | PROTECTION CLASS |  | IP65
32 | ■ | ALARM OUTPUT (3A AC250V/5A DC30V) | [8 empty] | CABLE SPECIFICATION |  | H05VV-F (6227 IEC53)
33 | WEIGHT |  |  | 2.6 | [5 empty] | kg | CABLE SIZE |  | 3C×0.75SQ×2m
34 | COLOR | [9 empty] | POWER PLUG |  | EUROPE 16A 250V
35 | HOUSING / PANEL |  |  | PANTONE 3125C / RAL7016 | [6 empty] | SPARE PAERTS
36 | ACCESSORIES | [9 empty] | □ | DIAPHRAGM |  | □ | BALL SEAT
37 | ■ | HOSE |  |  |  | ■ | SIPHON CHECK V/V |  |  |  | □ | CHECK BALL |  | □ | O-RING
38 | ■ | STRAINER FOOT V/V |  |  |  | □ | LEVEL SWITCH |  |  |  | □ | SPRING(VALVE)
39 | REMARKS:
40
CHEON SEI IND. CO., LTD.